## 615 Biennial Check
ABB RELION 615 SERIES — BIENNIAL (2-YEARLY) VISUAL CHECK SHEET (REF615 / RET615 / REM615 / REU615)
1. IED AND SITE INFORMATION
IED Model | REF615 / RET615 / REM615 / REU615 (circle one)
IED Configuration (A/B/C…) | e.g. REF615 C — from nameplate
Product Version | From LHMI: Information → Version (e.g. 5.0 FP1)
Protected Equipment
Site / Substation
IED Name / Bay | From LHMI home screen header
Panel / Cubicle Tag
Work Order No.
Date of Check
Technician Name
Next Check Due | (2 years from date above)
2. CONNECTION METHOD
OPTION A — LHMI only (no laptop): Navigate with keypad (ESC, arrows, Enter, Clear). Press any key to wake the display. Home screen shows the single-line diagram (SLD). OPTION B — Web HMI (WHMI) via laptop: Connect laptop Ethernet to front RJ-45 port (100Base-TX). Open web browser → navigate to IED IP address (find it at LHMI: Configuration → Communication → Ethernet). Login with VIEWER or OPERATOR credentials. NOTE: WHMI is disabled by default — confirm with site engineers before use. OPTION C — PCM600: Connect via front RJ-45 or substation Ethernet. Open PCM600, select relay in Plant Structure, use Online monitoring for live data.
Connection method used today | LHMI only / Web HMI (WHMI) / PCM600 (delete as applicable)
3. FRONT PANEL LED STATUS (visual check before connecting)
The 615 series has three fixed protection indicator LEDs above the display: READY (green) — START (yellow) — TRIP (red). Additionally, 11 programmable alarm LEDs on the right side of the display. IMPORTANT: READY LED flashing green = Internal fault (protection disabled). READY LED solid green = IED healthy and in service.
LED / Indicator | Expected State (healthy IED) | Observed State | Result (OK / FAULT) | Notes
READY LED (green) | Solid green — continuous, not flashing
START LED (yellow) | Off (or on if a protection element is picked up under load — may be normal)
TRIP LED (red) | Off (steady) — on only if latched trip not yet cleared
Progrm alarm LEDs (right side of display, LEDs 1–11) | All off, or known/accepted alarm conditions only
LHMI display — any 'Internal Fault' message visible? | No Internal Fault message on display
LHMI display — any 'Warning' message visible? | No Warning message, or known/accepted warning
4. SELF-SUPERVISION (Internal Faults and Warnings)
INTERNAL FAULT: Ready LED flashes. Protection is DISABLED. LHMI shows 'Internal Fault' with a numeric code (e.g. Code 80 = RAM error, Code 116 = COM card error). Record the code — relay requires restart or ABB support. WARNING: Ready LED stays solid green. Protection continues (functions affected by the fault may be impaired). LHMI shows 'Warning' with a name and code (e.g. Code 20 = IEC 61850 error, Code 35 = Comm. channel down). Record the code — warning message can be manually cleared after investigating.
Check Item | How to Check / LHMI Path | Expected | Result / Code | Action
Any 'Internal Fault' text on LHMI display? | LHMI home screen or press ESC to return to top level — fault message has highest LHMI priority | No Fault message
If fault: record fault code and description | Code is displayed alongside 'Internal Fault' message (Table 25 in Tech Manual for code list) | N/A if no fault
Any 'Warning' text on LHMI display? | LHMI home screen — Warning message appears with name and code | No Warning message
If warning: record warning code and name | Code displayed alongside 'Warning' message (Table 26 in Tech Manual for code list) | N/A if no warning
IRF (Internal fault relay) contact — X100 terminals 3-5 | Measure continuity across X100 terminals 3-5 (closed-circuit principle: CLOSED = healthy, OPEN = fault) | Contact CLOSED
5. ANALOGUE MEASUREMENTS (Primary Values — relay reports in primary units)
LHMI: Navigate to home screen (SLD). Live values may be shown on SLD (IL2, U12, P, Q). For full measurement view: LHMI → Monitoring → Measurements → Current measurements (or Voltage measurements). WHMI: Monitoring → Measurements (same data available via browser). Record measured primary values. Flag anything obviously abnormal (e.g. one phase zero while others are loaded).
Quantity | LHMI Path | Measured Value | Unit | Notes
IL1 — Phase L1 Current (primary) | Monitoring → Measurements → Current measurements → IL1 |  | A primary
IL2 — Phase L2 Current (primary) | Monitoring → Measurements → Current measurements → IL2 |  | A primary
IL3 — Phase L3 Current (primary) | Monitoring → Measurements → Current measurements → IL3 |  | A primary
I0 / IN — Residual Current | Monitoring → Measurements → Current measurements → I0 |  | A primary
UL1-L2 — Line Voltage (primary) | Monitoring → Measurements → Voltage measurements → U12 (if VT fitted) |  | kV primary
UL2-L3 — Line Voltage (primary) | Monitoring → Measurements → Voltage measurements → U23 (if VT fitted) |  | kV primary
UL3-L1 — Line Voltage (primary) | Monitoring → Measurements → Voltage measurements → U31 (if VT fitted) |  | kV primary
U0 — Residual Voltage | Monitoring → Measurements → Voltage measurements → U0 (if VT fitted) |  | V primary
Frequency | Monitoring → Measurements → Voltage measurements → f (if VT fitted) |  | Hz
P — Active Power | Monitoring → Measurements → Power measurements → P (if VT fitted) |  | kW primary
Q — Reactive Power | Monitoring → Measurements → Power measurements → Q (if VT fitted) |  | kVAr primary
Monitoring → Measurements
Monitoring → Measurements
Monitoring → Measurements
Monitoring → Measurements
Monitoring → Measurements
6. CLOCK AND TIME SYNCHRONISATION
LHMI: Configuration → Time → Date and Time (to view current date/time). Time sync source: Configuration → Time → Synch source (SNTP, IRIG-B, IEEE 1588 v2, Modbus, IEC 103, DNP or None). 48-hour capacitor backup keeps RTC running during power outages. If sync source = 'None', time is free-running and may drift — set manually if >10 s out.
Check | LHMI Path | IED Value | Reference | Difference / OK?
IED Date | Configuration → Time → Date |  | Today's date
IED Time | Configuration → Time → Time |  | Current time
Time sync source | Configuration → Time → Synch source |  | SNTP / IRIG-B /
Time sync status (GNRLTMS function block) | Monitoring → I/O status → GNRLTMS → ALARM / WARNING output signals |  | ALARM & WARNING = False
Time difference (accept ≤ 10 s if internal; ≤ 1 s if SNTP/IRIG-B) | Compare LHMI time display to GPS/phone reference |  | ≤ 10 s
7. RECENT EVENTS (record most recent events — flag any unexplained trips or alarms)
LHMI: Navigate to Events (press Events button or use menu → Events → Event list). Events are stored newest first (FIFO — 1024 process events, 2048 audit trail events in nonvolatile memory). WHMI: Events menu at top of screen — same data, easier to scroll. PCM600: Event Viewer for full event list including audit trail. Flag any unexplained TRIP, OPERATE or FAULT events for investigation.
Event # (most recent = 1) | Date | Time | Event Description / Function
1
2
3
4
5
6
7
8
9
10
11
12
Total events in event list (approximate)
8. DCS / ABB 800XA COMMUNICATION CHECK
Open the IED faceplate in the ABB 800XA control system. Verify live values (currents, IED status) are updating and not frozen. The 615 series communicates via IEC 61850 (primary), IEC 60870-5-103 or Modbus to the 800XA. Check for any yellow or red communication alarm objects on the 800XA faceplate. Record the 800XA object path for reference.
Check | Description | Result (Y / N) | Notes
800XA faceplate opened | Navigate to IED faceplate in 800XA Plant Explorer
IED Status = HEALTHY / OK on faceplate | Status indicator green — not alarm/fault colour
Live phase current values updating | Active Measured currents on faceplate match LHMI readings
No IEC 61850 / Modbus communication alarm | No yellow or red comms alarm objects on 800XA faceplate
Record 800XA object path / faceplate name | e.g. 'Site / Substation / Bay / Relay faceplate'
9. OPTIONAL — CLEAR EVENTS / INDICATIONS (only if required by site procedure)
Requires ENGINEER or ADMINISTRATOR access level. Download / record all events BEFORE clearing. LHMI: Clear menu (bottom of main menu or dedicated Clear button) → Event list → Clear all. WHMI: Events menu → select events → Clear. Trip/start indications: LHMI Clear menu → Trip indications / Start indications. WARNING indications: can be manually cleared from LHMI display when Warning message is shown.
Action | LHMI / WHMI Path | Performed? (Y / N / N/A) | Notes
Download event list before clearing | WHMI: Events → Export, or PCM600: Event Viewer → Save
Clear event list | LHMI: Clear → Event list → Clear all (requires ENGINEER access)
Clear trip / start LED indications | LHMI: Clear → Trip indications OR press Clear button on keypad
Clear warning indication (if present) | Press any key when Warning message displayed, or LHMI: Clear → Indications
Clear disturbance records (if required) | LHMI: Clear → Disturbance records (requires ENGINEER access)
10. OBSERVATIONS AND CORRECTIVE ACTIONS
11. SIGN-OFF
Role | Name (print) | Signature | Date
Technician
Supervisor / Witness
Note on A37: May be if it is safe to do open a link to check the alarm ot DCS