## 670 Check Sheet
ABB RELION 670 IED — BIENNIAL (2-YEARLY) VISUAL CHECK SHEET (REG670 / RET670)
1. IED AND SITE INFORMATION
IED Model | REG670 / RET670 (circle one)
Protected Equipment
Site / Substation
IED Name (Station / Bay)
Panel / Cubicle Tag
Work Order No.
Date of Check
Technician Name
Next Check Due | (2 years from date above)
2. CONNECTION METHOD
OPTION A — LHMI only (no laptop): The RET/REG670 has a full graphical touchscreen or keypad LHMI. Navigate with arrow keys / touchscreen. Main menu accessible from the LHMI home screen. OPTION B — Ethernet + PCM600 laptop: Connect laptop Ethernet to IED front port (RJ45). Open PCM600 → Online > Signal Monitor for live values. IP address from LHMI: Main menu → Settings → Communication → Ethernet. OPTION C — Ethernet + web browser: Navigate to IED IP address in browser (if web server enabled).
Connection method used today | LHMI only / Ethernet + PCM600 / Ethernet + browser (delete as applicable)
3. SELF-TEST AND IED STATUS (INTERRSIG self-supervision)
LHMI path: Main menu → Diagnostics → IED status → Signals → INTERRSIG. All signals should show NORMAL (0). A FAIL signal asserts the INTERNAL FAIL contact on the PSM. Hardware modules: Main menu → Diagnostics → Hardware → Module status.
Check Item | LHMI Path / How to Read | Expected | Result | Notes
Normal LED (green, fixed) | Visual — front panel upper-left LED | Green, solid
No alarm LEDs active | Visual — front panel LED indicators (15 programmable LEDs) | All off (or known/accepted)
INTERRSIG — FAIL signal | LHMI: Main menu → Diagnostics → IED status → Signals | NORMAL (0)
INTERRSIG — WARNING signal | Same path as above | NORMAL (0)
INTERRSIG — RTCERROR (clock error) | Same path as above | NORMAL (0)
INTERRSIG — TIMESYNCHERROR | Same path as above | NORMAL (0)
INTERRSIG — WATCHDOG | Same path as above | NORMAL (0)
INTERNAL FAIL contact (PSM terminal) | Measure across PSM INTERNAL FAIL output terminals | Contact OPEN (IED healthy)
PSM module status | LHMI: Main menu → Diagnostics → Hardware | OK
BIM / BOM / TRM module status | LHMI: Main menu → Diagnostics → Hardware | OK
Internal events — any recent FAILs? | LHMI: Main menu → Diagnostics → IED status → Internal events | No unexplained FAIL events
4. ANALOGUE MEASUREMENTS (Primary Values)
LHMI: Main menu → Measurements → [function block, e.g. T2WPDIF, GENPDIF, OC4PTOC] → monitored data. All values displayed in primary units. Record current load values below. PCM600: Signal Monitor shows live primary values.
Quantity | LHMI Path / Function Block | Measured Value | Unit | Notes
IA — Phase A Current (W1) | Measurements → [SMAI/CT function] → IA |  | A primary
IB — Phase B Current (W1) | Measurements → [SMAI/CT function] → IB |  | A primary
IC — Phase C Current (W1) | Measurements → [SMAI/CT function] → IC |  | A primary
IA — Phase A Current (W2 / Y-side) | Measurements → [SMAI W2] → IA (if 2nd CT set) |  | A primary
IB — Phase B Current (W2 / Y-side) |  |  | A primary
IC — Phase C Current (W2 / Y-side) |  |  | A primary
VA — Phase A Voltage | Measurements → [voltage function] → VA (if VT fitted) |  | kV primary
VB — Phase B Voltage | (if VT fitted) |  | kV primary
VC — Phase C Voltage | (if VT fitted) |  | kV primary
Frequency | Measurements → [voltage function] → frequency |  | Hz
5. CLOCK AND TIME SYNCHRONISATION
Check | LHMI Path | IED Value | Reference | Difference / OK?
IED Date and Time | Main menu → Diagnostics → IED status → Time (or Configuration → Time) |  | Today's date / time
Time source (IRIG-B / IEEE 1588 / NTP) | Main menu → Diagnostics → IED status → Time source |  | IRIG-B or IEEE 1588
TIMESYNCHERROR = NORMAL | Main menu → Diagnostics → IED status → Signals |  | NORMAL
Time difference (accept ≤ 1 s with sync; ≤ 10 s internal) | Compare LHMI time to GPS/phone reference |  | ≤ 1 s
6. RECENT EVENTS (record most recent disturbance records / events)
LHMI: Main menu → Events → Disturbance records list (most recent first). PCM600: Event viewer shows all logged events with timestamps. Record the most recent events; flag any unexplained trips or alarms.
Event # (most recent = 1) | Date | Time | Event Description / Type
1
2
3
4
5
6
7
8
9
10
11
12
Total disturbance records (as displayed on LHMI)
7. DCS / ABB 800XA COMMUNICATION CHECK
Open the IED faceplate in the ABB 800XA control system. Verify live values (currents, IED status indicators) are updating. The 800XA communicates via IEC 61850 GOOSE / MMS. No yellow or red communication alarm objects should be present.
Check | Description | Result (Y / N) | Notes
800XA faceplate opened | Navigate to IED faceplate in 800XA Plant Explorer
IED Status = HEALTHY / OK | Green status indicator on faceplate — not alarm/fault colour
Live current values updating | Measured currents on faceplate match LHMI readings
No communication alarm | No yellow/red GOOSE or MMS communication alarm objects
800XA object path (record below) | e.g. 'Site / Substation / Relay Tag / Faceplate'
8. OPTIONAL — CLEAR EVENT BUFFERS (only if required by your procedure)
Only clear events if required by site procedure. Ensure all events have been downloaded/recorded BEFORE clearing. LHMI: Main menu → Events → [select event] → Clear (or Clear all). Internal events (INTERRSIG log) clear automatically after 40 events (FIFO).
Action | LHMI Path | Performed? (Y / N / N/A) | Notes
Download disturbance records | PCM600 → Disturbance handling → Save to file
Clear disturbance records | LHMI: Main menu → Events → Clear disturbance records
9. OBSERVATIONS AND CORRECTIVE ACTIONS
10. SIGN-OFF
Role | Name (print) | Signature | Date
Technician
Supervisor / Witness