## GE 889 Biennial Check
GE MULTILIN 889 GENERATOR PROTECTION SYSTEM — BIENNIAL (2-YEARLY) VISUAL CHECK SHEET
1. RELAY AND SITE INFORMATION
Relay Model | GE Multilin 889 Generator Protection System
Protected Equipment
Site / Substation
Equipment Tag (relay)
Order Code / Part Number
Serial Number
Firmware Version | (record from Status → Information → Main CPU)
Panel / Cubicle Tag
Work Order No.
Date of Check
Technician Name
Next Check Due | (2 years from date above)
2. CONNECTION METHOD
OPTION A — Front panel only (no laptop): Press any key to wake the graphical display. Navigate using the keypad and function keys. OPTION B — EnerVista 8 Series Setup Software via Ethernet (RJ45 port on rear): Launch EnerVista, add relay (File → New Device), enter relay IP address. Right-click device → Quick Connect. Default Modbus TCP port: 502. OPTION C — USB local programming port (front panel): Connect USB cable; EnerVista detects via USB.
Connection method used today | Front panel / EnerVista Ethernet / EnerVista USB (delete as applicable)
3. SELF-TEST AND DEVICE STATUS
Front panel: Status → Device Status. All items should show OK — no warnings or faults. Normal LED (green, solid) must be illuminated. Warning LED (amber) or Critical LED (red) indicates a condition requiring investigation before returning to service. EnerVista: Actual Values → Status → Device Status.
Check Item | How to Read / Navigation Path | Expected | Result | Notes
Normal LED (green, solid) | Visual — front panel top-left LED indicator | ON solid green
Warning LED (amber) | Visual — front panel LED | OFF — no warnings
Critical LED (red) | Visual — front panel LED | OFF — no critical faults
Device Status — no active faults | Front panel: Status → Device Status EnerVista: Actual Values → Status → Device Status | All OK
Main CPU self-test | Front panel: Status → Information → Main CPU | No errors
Comms CPU self-test | Front panel: Status → Information → Comms CPU | No errors
Hardware module health | Front panel: Status → Information → Hardware Versions | All modules present
Record firmware version | Front panel: Status → Information → Main CPU → Firmware | Record version
Modbus TCP communications active | Front panel: Status → Communications EnerVista: connected and updating | Comms healthy
4. ANALOGUE MEASUREMENTS (Primary Values — relay reports in primary units)
Front panel: Metering → Currents (for phase and ground currents in primary A). Metering → Voltages (for phase voltages in primary kV). Metering → Frequency (Hz). EnerVista: Actual Values → Metering → Currents / Voltages / Frequency. Record measured values. No specific pass/fail for 2-yearly check — flag anything obviously wrong (e.g. one phase zero, both CT banks disagree).
Quantity | Navigation Path | Measured Value | Unit | Notes
IA_J — Phase A (neutral-side CT, J1) | Metering → Currents |  | A primary
IB_J — Phase B (neutral-side CT, J1) | Metering → Currents |  | A primary
IC_J — Phase C (neutral-side CT, J1) | Metering → Currents |  | A primary
IA_K — Phase A (terminal-side CT, K1) | Metering → Currents |  | A primary
IB_K — Phase B (terminal-side CT, K1) | Metering → Currents |  | A primary
IC_K — Phase C (terminal-side CT, K1) | Metering → Currents |  | A primary
IN — Ground / CBCT current | Metering → Currents |  | A primary
Va-n — Phase A voltage | Metering → Voltages |  | kV primary
Vb-n — Phase B voltage | Metering → Voltages |  | kV primary
Vc-n — Phase C voltage | Metering → Voltages |  | kV primary
Frequency | Metering → Frequency |  | Hz
87G IOP (operate current, Phase A) | Metering → Generator → Percent Differential |  | pu (accept ≤ 0.05)
Metering → …
Metering → …
Metering → …
Metering → …
5. CLOCK AND TIME SYNCHRONISATION
Check | Navigation Path | Relay Value | Reference Value | Difference / Result
Relay Date | Front panel: Status → Clock EnerVista: Actual Values → Status → Clock |  | Today's date
Relay Time | Front panel: Status → Clock EnerVista: Actual Values → Status → Clock |  | GPS / NTP reference
Time synchronisation source | Front panel: Status → Clock or Status → PTP Status |  | SNTP or IRIG-B preferred
Time difference (accept ≤ 10 s) | Relay time vs phone / GPS reference clock |  | ≤ 10 s
6. RECENT EVENTS (record most recent events — flag any unexplained trips or alarms)
Front panel: Records → Events. Navigate to event list and scroll through entries. EnerVista: Records → Events — export or view event list. Record the most recent events. Flag any unexplained trips, alarms, or self-test events.
Event # (most recent = 1) | Date | Time | Event Description / Type
1
2
3
4
5
6
7
8
9
10
11
12
Total events since last check (approx.)
7. DCS / MODBUS TCP COMMUNICATION CHECK (800XA)
Open the relay faceplate in ABB 800XA. Verify that live values (currents, voltages, status) are updating and not frozen. Check for any Modbus communication alarm objects (yellow/red). The 889 communicates via Modbus TCP on port 502 (default). Record the 800XA object path or faceplate name below.
Check | Description | Result (Y / N) | Notes
800XA faceplate opened | Navigate to relay faceplate in ABB 800XA control system
Live values updating | Phase currents / voltages / status visible and updating with load
No Modbus TCP communication alarm | No yellow or red communication alarm objects on faceplate
Status objects correct | Relay status (Normal/Warning/Critical) visible and correct in 800XA
Record 800XA object path / faceplate name | e.g. "Site/Substation/Relay Tag/Faceplate"
8. OPTIONAL — CLEAR RECORDS (only if required by procedure — confirm with engineer)
If your site procedure requires clearing event records after the biennial check, navigate to: Front panel: Records → Clear Records. EnerVista: Records → Clear Records. Ensure all events have been downloaded / recorded BEFORE clearing.
Record Type | Navigation Path | Performed? (Y / N / N/A) | Notes
Events | Front panel: Records → Clear Records → Events EnerVista: Records → Clear Records
Transient Records (if required) | Front panel: Records → Clear Records → Transients
Fault Reports (if required) | Front panel: Records → Clear Records → Fault Reports
9. OBSERVATIONS AND CORRECTIVE ACTIONS
10. SIGN-OFF
Role | Name (print) | Signature | Date
Technician
Supervisor / Witness