## SEL Biennial Check
SEL PROTECTION RELAY — BIENNIAL (2-YEARLY) VISUAL CHECK SHEET
1. RELAY AND SITE INFORMATION
Relay Model | SEL-300G / SEL-311L / SEL-787 / SEL-700G (circle one)
Protected Equipment
Site / Substation
Relay ID (RID / TID)
Panel / Cubicle Tag
Work Order No.
Date of Check
Technician Name
Next Check Due | (2 years from date above)
2. CONNECTION METHOD
OPTION A — Front panel only (no laptop): Press any key to wake display. Navigate with arrow keys. OPTION B — Serial cable: Connect SEL-C662 cable (laptop USB → relay front DB-9). Open PuTTY/terminal: 19200 baud, 8-N-1, no flow control. Press Enter → prompt appears. Type ACC <Enter>, enter Level 1 password (default: OTTER). OPTION C — Ethernet (if fitted): Open AcSELerator QuickSet or SSH/Telnet to relay IP.
Connection method used today | Front panel / Serial cable / Ethernet (delete as applicable)
3. SELF-TEST AND DEVICE STATUS
Front panel: ENABLED LED (green, solid) must be illuminated. Serial: type STA <Enter> or STATUS <Enter> — all items should show OK. W = warning (issue STA C to clear), FAIL = fault (requires investigation).
Check Item | How to Read / Where to Look | Expected | Result | Notes
ENABLED LED (green, solid) | Visual — front panel top-right LED | ON (solid green)
No alarm LEDs active | Visual — front panel LEDs | All alarm LEDs off
Front panel display | Visual — press any key to wake | No error messages shown
Self-test status — all OK | Serial: STA <Enter> Front panel: Main > Status | All items = OK
HALARM bit (hardware alarm) | STA output: look for HALARM = 0 | 0 (not asserted)
SALARM bit (software alarm) | STA output: look for SALARM = 0 | 0 (not asserted)
Relay shows 'Relay Enabled' | Last line of STA output | 'Relay Enabled'
4. ANALOGUE MEASUREMENTS (Primary Values — relay reports in primary units)
Serial: type METER <Enter> — relay displays primary values (A and V). Front panel: Main > Meters > Fundamental. Record measured values. Compare to expected load (no specific pass/fail for 2-yearly — flag anything obviously wrong, e.g., one phase zero when others are normal).
Quantity | Reading Method | Measured Value | Unit | Notes
IA — Phase A Current (primary) | METER / Meters > Fundamental |  | A primary
IB — Phase B Current (primary) | METER / Meters > Fundamental |  | A primary
IC — Phase C Current (primary) | METER / Meters > Fundamental |  | A primary
IN / IGX — Residual / Neutral | METER / Meters > Fundamental |  | A primary
VA — Phase A Voltage (primary) | METER / Meters > Fundamental (if VT fitted) |  | kV primary
VB — Phase B Voltage (primary) | METER / Meters > Fundamental (if VT fitted) |  | kV primary
VC — Phase C Voltage (primary) | METER / Meters > Fundamental (if VT fitted) |  | kV primary
Frequency | METER / Meters > Fundamental |  | Hz
METER / Meters > Fundamental
METER / Meters > Fundamental
METER / Meters > Fundamental
METER / Meters > Fundamental
METER / Meters > Fundamental
METER / Meters > Fundamental
5. CLOCK AND TIME SYNCHRONISATION
Check | How to Read | Relay Value | Reference Value | Difference / Result
Relay Date | Serial: DAT <Enter> Front panel: Main > Time or Status |  | Today's date
Relay Time | Serial: TIM <Enter> Front panel: Main > Time or Status |  | GPS/NTP reference
Time source (IRIG-B / NTP / Internal) | Serial: STA <Enter> — look for IRIG-B or NTP line |  | IRIG-B preferred
Time difference (accept ≤ 10 s) | Relay time vs phone/GPS reference |  | ≤ 10 s
6. RECENT EVENTS (record most recent events — flag any unexplained trips or alarms)
Serial: type HIS <Enter> for event history, or EVE <Enter> for last event report, or SER <Enter> for Sequential Events Recorder. Front panel: Main > Events (or Main > Targets for relay word bits). Record the most recent events and their dates below.
Event # (most recent = 1) | Date | Time | Event Description / Type
1
2
3
4
5
6
7
8
9
10
11
12
Total events since last check (approx.)
7. DCS / 800XA COMMUNICATION CHECK
Open the relay faceplate in ABB 800XA. Verify that live values (currents, status) are updating and not frozen. Check for any communication alarm objects (yellow/red). Record the 800XA object path or faceplate name below.
Check | Description | Result (Y / N) | Notes
800XA faceplate opened | Navigate to relay faceplate in 800XA control system
Live values updating | Phase currents / status visible and changing with load.
No communication alarm | No yellow or red communication alarm objects on faceplate
Record 800XA object path / faceplate name | e.g. "Site/Substation/Relay Tag/Faceplate"
8. OPTIONAL — CLEAR EVENT BUFFERS (only if required by your procedure)
If your site procedure requires clearing event buffers after recording, issue the following serial commands at Access Level 1 or 2. Ensure all events have been downloaded/recorded BEFORE clearing.
Serial Command | Action | Performed? (Y / N / N/A) | Notes
SUM R <Enter> | Reset event report and Summary Command buffers
SER R <Enter> | Reset Sequential Events Record buffer
HIS C <Enter> | Clear event history (if required — confirm with supervisor)
9. OBSERVATIONS AND CORRECTIVE ACTIONS
10. SIGN-OFF
Role | Name (print) | Signature | Date
Technician
Supervisor / Witness