PROTECTION RELAY TEST CHECK SHEET

ABB Relion REG670 2.0 (ANSI) Generator Protection IED

Routine / Maintenance Test Procedure

## Document Control

| Revision | Date | Description | Prepared By | Approved By |
| --- | --- | --- | --- | --- |
| 1.0 |  | Initial issue |  |  |

## Test Summary & Findings

Filled in by the tester at the end of the visit. Captures the overall outcome and any noteworthy findings.

| Overall test result | ☐ PASS — IED returned to service ☐ PASS with defects (see findings) ☐ FAIL / withdrawn |
| --- | --- |
| Test completion date |  |
| Summary & key findings |  |
| Self-supervision status on departure | ☐ Normal (green) LED steady, no FAIL/WARNING ☐ Issue noted (see findings) |

# 1. Test Information

### 1.1 Site & Project

| Site / Power station |  |
| --- | --- |
| Asset identifier (generator / unit) |  |
| Work order / Job number |  |
| Reason for test | Routine / Maintenance |
| Test date (start) |  |
| Test date (finish) |  |

### 1.2 Personnel

| Tester (name) |  |
| --- | --- |
| Tester signature |  |
| Witness / 2nd person |  |
| Witness signature |  |
| Authorising engineer |  |

### 1.3 IED Under Test

| IED model | ABB Relion REG670 2.0 (ANSI) |
| --- | --- |
| IED tag / functional ID |  |
| Serial number (SerialNo) |  |
| Ordering number (OrderingNo) |  |
| Firmware version (FirmwareVer) |  |
| Product version (ProductVer) |  |
| Production date (ProductionDate) |  |
| Panel / cubicle location |  |
| Main VT ratio (primary : secondary) | _____ kV : _____ V |
| Neutral VT ratio (primary : secondary) | _____ V : _____ V |
| Generator terminal CT ratio (primary : secondary) | _____ A : _____ A |
| Generator neutral CT ratio (primary : secondary) | _____ A : _____ A |
| Global base voltage (VBase) | _____ kV |
| Global base current (IBase) | _____ A |
| Active setting group | GRP _____ (1–6) |
| PCM600 project file name |  |
| Notes |  |

### 1.4 Test Equipment

NOTE: All injection equipment must be within calibration. Record calibration certificate numbers and due dates below.

| Equipment | Make / Model | Serial No. | Last Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- |
| Three-phase test set | Omicron CMC |  |  |  |
| Laptop (PCM600) |  |  |  |  |
| 20 Hz injection set (64S/64R) | ABB REX060 / equiv. |  |  |  |

### 1.5 Reference Drawings

| Drawing No. | Title | Revision | Date |
| --- | --- | --- | --- |
|  | Single line diagram |  |  |
|  | AC schematic / CT-VT |  |  |
|  | DC schematic / trip |  |  |
|  | Binary I/O allocation |  |  |

### 1.6 Test File & Reference Document Locations

Record the Omicron test file name and SharePoint locations for the key project documents (PCM600 project, settings, functional description, drawings).

| Omicron test file (.occ) |  |
| --- | --- |
| PCM600 project file (.pcmp / .pcmi) |  |
| SharePoint — Settings folder |  |
| SharePoint — Functional description |  |
| SharePoint — Drawings |  |

# 2. Safety, Isolations & Permits

Confirm the following before commencing any test work on the IED or its secondary circuits.

☐  Permit to work / switching certificate received and read.

☐  Plant electrically isolated; circuit breaker(s) racked-out and locked-out (LOTO applied).

☐  VT secondary circuits isolated; VT MCBs OFF or links removed (mark each link removed).

☐  CT secondary circuits short-circuited at the test block before disconnection. Verify shorting.

☐  Trip and lockout outputs disabled / links removed to prevent unintended operation of plant.

☐  Trip lockout (86G) and master trip relays disabled where required. Record state below.

☐  64S / 64R sub-harmonic injection systems (REX060) blocked / isolated for testing if required.

☐  Adjacent live equipment identified; barriers / signs in place.

☐  Correct PPE: arc-rated clothing, insulating gloves, eye protection, safety footwear.

☐  Test leads inspected; no damaged insulation; correct ratings.

☐  Earth bond between test set and IED panel earth bar verified.

☐  Communications to SCADA / DCS (IEC 61850 / GOOSE) inhibited or operations notified to suppress alarms.

### 2.1 Isolation Record

| Isolation point | Tag / Reference | State left | Time | Initials |
| --- | --- | --- | --- | --- |

# 3. Pre-Test Checks

## 3.1 Visual Inspection

☐  IED is mounted securely; no physical damage to fascia (LHMI) or terminals.

☐  LHMI display, push-buttons and LEDs all illuminate during lamp test.

☐  All wiring terminations tight (sample check); no signs of overheating or discolouration.

☐  No active alarm LEDs or messages on arrival. Record any present below.

☐  Auxiliary supply voltage at PSM terminals within tolerance (record value).

☐  INTERNAL FAIL contact wiring on the PSM intact and correctly terminated.

## 3.2 Connect to IED & Verify Status

☐  Connect via LHMI (RJ-45 front port) or PCM600 via Ethernet (rear).

☐  Verify the “Normal” green status LED (above the LCD) is lit and steady — IED healthy.

☐  Check Main menu → Diagnostics → IED status → General: no FAIL or WARNING active.

☐  Record firmware version from Main menu → Diagnostics → IED status → Product identifiers.

☐  Record IEDProdType, ProductVer, SerialNo, OrderingNo, ProductionDate, FirmwareVer.

☐  Compare firmware version against the plant register.

| “Normal” green LED state | ☐ Lit & steady (healthy) ☐ Off / flashing (investigate) |
| --- | --- |
| IED status — General | ☐ No FAIL / WARNING ☐ Signal active (record below) |
| Firmware version read |  |
| Matches plant register? | ☐ Yes ☐ No (raise finding) |

## 3.3 Self-Supervision Review  (ABB-specific)

NOTE: The REG670 runs continuous hardware and software self-supervision. This is a key differentiator from the SEL-300G and MUST be reviewed every visit. The INTERRSIG function block reports the software status; the potential-free INTERNAL FAIL contact on the PSM reports the hardware status.

☐  Navigate to Main menu → Diagnostics → Internal events (last 40 events, FIFO).

☐  Review and record ALL internal events since the last test visit.

☐  Confirm no active FAIL, WARNING, RTCERROR, TIMESYNCHERROR, RTEERROR, IEC61850ERROR, WATCHDOG, LMDERROR or APPERROR signals (Diagnostics → IED status → General).

☐  Check for module-specific errors: PSM-Error, ADOne-Error, BIM-Error, BOM-Error, IOM-Error, MIM-Error, LDCM-Error.

☐  Check the INTERNAL FAIL contact on the PSM is de-energised (i.e. IED healthy).

☐  Verify no alarm LEDs are lit that indicate a self-supervision issue.

☐  Record overall self-supervision status (All OK / active events noted).

| INTERRSIG signal | State (Active / Inactive) | Notes |
| --- | --- | --- |
| FAIL (Internal Fail) |  |  |
| WARNING (Internal Warning) |  |  |
| RTCERROR (RTC hardware) |  |  |
| TIMESYNCHERROR (time sync lost) |  |  |
| RTEERROR (runtime execution) |  |  |
| IEC61850ERROR (61850 stack) |  |  |
| WATCHDOG (heavy CPU >5 min) |  |  |
| LMDERROR (LON interface) |  |  |
| APPERROR (application thread) |  |  |

| INTERNAL FAIL contact (PSM) | ☐ De-energised (healthy) ☐ Asserted (fault) |
| --- | --- |
| Internal events since last visit | ☐ None ☐ Recorded (attach list) |
| Overall self-supervision status | ☐ All OK ☐ Active events noted (raise finding) |

### 3.3.1 Internal Events Log (record since last visit)

| # | Date / Time | Internal event / signal | Action taken |
| --- | --- | --- | --- |

## 3.4 Time / Clock Check

☐  Navigate to Main menu → Diagnostics → IED status → General for RTC status.

☐  Compare IED clock with GPS / station reference time source.

☐  Note the TIMESYNCHERROR signal state.

☐  Record the configured time source (Main menu → Settings → Time).

NOTE: The RTC is capacitor-backed. After ~5 days powered-off the clock may drift around 3 s/day and can reset. Record drift and correct at end of visit if outside tolerance (typically ±1 s).

| Reference time source | ☐ GPS ☐ IRIG-B ☐ SNTP ☐ LON ☐ SPA ☐ BIN |
| --- | --- |
| IED time (read) |  |
| Reference time |  |
| Drift (s) |  |
| TIMESYNCHERROR state | ☐ Inactive ☐ Active |

## 3.5 Download Event Records

☐  Export events via LHMI → Events or PCM600 Event Viewer.

☐  Save with naming convention: YYYYMMDD_[IED tag]_EVE_asfound.

☐  Review for unexpected pickups, operations or binary-input chatter since last visit.

☐  Cross-reference any abnormal events with operations / SCADA log.

## 3.6 Download Disturbance Records

☐  LHMI → Disturbance records (DRPRDRE): download all records since last visit via PCM600.

☐  Save with naming convention: YYYYMMDD_[IED tag]_DIST_asfound.

☐  Review waveforms for any anomalies or unexplained operations.

## 3.7 Settings — As-Found

☐  Open PCM600, connect to the IED and upload (read) the current settings.

☐  Save the PCM600 project as: asfound_[date]_[IED tag].pcm.

☐  Compare against the approved master settings.

☐  Document every difference. If unauthorised changes are found, STOP and notify the asset owner.

| As-found project file name |  |
| --- | --- |
| Master settings reference |  |
| Differences found (Y/N) |  |

| # | Setting / Parameter | Master value | As-found value | Authorised? (Y/N) |
| --- | --- | --- | --- | --- |

## 3.8 Settings vs. Protection Functional Description

☐  Open the latest approved Protection Functional Description for this asset.

☐  Verify enabled functions on the IED align with those required by the document.

☐  Spot-check key element settings (pickup, time delay, characteristic) against the document.

☐  Confirm trip matrix / SMBO output mapping matches the functional description.

☐  Confirm CT / VT ratios and VBase / IBase match nameplate / SLD and section 1.3 above.

☐  Record the active setting group (GRP 1–6).

| Functional description rev. |  |
| --- | --- |
| Active setting group | GRP _____ |
| Discrepancies found (Y/N) |  |

# 4. Analogue Input Verification

The REG670 uses SMAI (Signal Matrix for Analog Inputs) preprocessing and reports PRIMARY values via the Measurements menu. Inject known secondary signals from the test set and read the PRIMARY value reported by the IED.

NOTE: All measurements below are PRIMARY values read from Main menu → Measurements. Expected Primary = injected secondary × configured ratio (VBase / IBase scaling applies). The xlsx template computes Expected Primary, error % and pass/fail automatically.

## 4.1 Main VT Inputs — Three-Phase Voltage Injection

Inject balanced three-phase secondary voltage (L1/L2/L3). Read primary from Main menu → Measurements.

☐  Test block links / VT MCBs isolated; injection leads connected to IED terminals.

☐  Phase rotation set to ABC (or as installed).

| Step | Injected (V sec) | Angle (°) | Phase / Input | Expected Primary | Relay Primary Reported | Relay Angle (°) | Mag Err % | P/F |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 63.5 | 0 | L1 (VA) |  |  |  |  |  |
| 1 | 63.5 | -120 | L2 (VB) |  |  |  |  |  |
| 1 | 63.5 | 120 | L3 (VC) |  |  |  |  |  |
| 2 | 30 | 0 | L1 (VA) |  |  |  |  |  |
| 2 | 30 | -120 | L2 (VB) |  |  |  |  |  |
| 2 | 30 | 120 | L3 (VC) |  |  |  |  |  |

## 4.2 Neutral VT Input — Generator Neutral Voltage (VN)

Inject single-phase voltage into the dedicated neutral-voltage input.

| Step | Injected (V sec) | Angle (°) | Phase / Input | Expected Primary | Relay Primary Reported | Relay Angle (°) | Mag Err % | P/F |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 10 | 0 | VN |  |  |  |  |  |
| 2 | 30 | 0 | VN |  |  |  |  |  |
| 3 | 60 | 0 | VN |  |  |  |  |  |
| 4 | 100 | 0 | VN |  |  |  |  |  |

## 4.3 Generator Terminal CT — Three-Phase Current Injection

Inject balanced three-phase current into the stator / terminal-side CT inputs (L1/L2/L3).

☐  CT shorting links applied at test block; relay-side connected to test set.

☐  Phase rotation ABC; angles per below.

| Step | Injected (V sec) | Angle (°) | Phase / Input | Expected Primary | Relay Primary Reported | Relay Angle (°) | Mag Err % | P/F |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 1 | 0 | L1 terminal |  |  |  |  |  |
| 1 | 1 | -120 | L2 terminal |  |  |  |  |  |
| 1 | 1 | 120 | L3 terminal |  |  |  |  |  |
| 2 | 5 | 0 | L1 terminal |  |  |  |  |  |
| 2 | 5 | -120 | L2 terminal |  |  |  |  |  |
| 2 | 5 | 120 | L3 terminal |  |  |  |  |  |

## 4.4 Generator Neutral CT — Three-Phase Current Injection

Inject balanced three-phase current into the neutral-side CT inputs (used by 87G GENPDIF).

☐  Confirm correct terminal block — neutral-side inputs.

☐  Polarity matches terminal-side injection so 87G operating current ≈ 0 with both sides equal.

| Step | Injected (V sec) | Angle (°) | Phase / Input | Expected Primary | Relay Primary Reported | Relay Angle (°) | Mag Err % | P/F |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 1 | 0 | L1 neutral |  |  |  |  |  |
| 1 | 1 | -120 | L2 neutral |  |  |  |  |  |
| 1 | 1 | 120 | L3 neutral |  |  |  |  |  |
| 2 | 5 | 0 | L1 neutral |  |  |  |  |  |
| 2 | 5 | -120 | L2 neutral |  |  |  |  |  |
| 2 | 5 | 120 | L3 neutral |  |  |  |  |  |

## 4.5 87G Differential Stability (Through-Current Injection)

Inject balanced three-phase through-current into both terminal-side and neutral-side CT inputs simultaneously. Verify differential current Id ≈ 0 and bias current Ibias ≈ rated. Read from Main menu → Measurements (GENPDIF).

| Phase | Terminal I (A pri) | Neutral I (A pri) | Id operating (A) | Ibias (A) | Acceptable? |
| --- | --- | --- | --- | --- | --- |
| L1 |  |  |  |  |  |
| L2 |  |  |  |  |  |
| L3 |  |  |  |  |  |

# 5. Binary Input / Output Functional Tests

The REG670 maps physical I/O via SMBI (binary inputs) and SMBO (binary outputs) function blocks. Actual labels are site-specific — fill from the binary I/O allocation drawing.

## 5.1 Binary Inputs (SMBI)

Apply rated voltage to each input (or operate the source field device) and confirm assertion via LHMI / PCM600 signal monitoring.

| Input | Description / Source (site drawing) | Pickup V (V) | Asserted? (Y/N) | Event captured? (Y/N) | Initials |
| --- | --- | --- | --- | --- | --- |
| BI01 | 86G lockout relay asserted |  |  |  |  |
| BI02 | Plant available / off-line |  |  |  |  |
| BI03 | Generator breaker open |  |  |  |  |
| BI04 | Exciter breaker open |  |  |  |  |
| BI05 | Test mode enable |  |  |  |  |
| BI06 | REF695 block (if applied) |  |  |  |  |

## 5.2 Binary Outputs (SMBO)

Force each output via PCM600 test / signal forcing, or by asserting the driving element. Verify continuity and target-device operation.

NOTE: Trip and lockout outputs MUST remain disabled at the panel / lockout relay if plant cannot tolerate an operation.

| Output | Driven by / Function (site drawing) | Force method | Continuity (Y/N) | Operates target (Y/N) | Initials |
| --- | --- | --- | --- | --- | --- |
| BO01 | Trip Generator Breaker (87G/87T/27/59) | PCM600 force |  |  |  |
| BO02 | Trip Exciter Breaker (40) | PCM600 force |  |  |  |
| BO03 | Trip & Lockout 86G | PCM600 force |  |  |  |
| BO04 | Alarm | PCM600 force |  |  |  |
| BO05 | INTERNAL FAIL (INTERRSIG FAIL) | PCM600 force |  |  |  |

# 6. Protection Element Testing (Omicron)

## 6.1 Test File Structure

Inside the Omicron Test Universe (.occ) file for this asset, create one folder/section per protection element tested. Each should contain:

A document block listing the as-applied settings (pickup, time delay, characteristic, restraint, blocking).

Tester instructions: how to inject (currents, voltages, angles, fault types) and what to block to isolate the element.

The test modules (ramp, shot, sequencer, etc.) configured for that element.

A results table recording measured pickup, drop-out, operate time and pass/fail.

NOTE: Keep folder naming consistent — recommended “<ANSI>_<ABB function>” (e.g. 87G_GENPDIF, 40_LEXPDIS).

## 6.2 Element Selection Strategy

It is not necessary to test every enabled element on each visit. Rotate elements so coverage is achieved over time. Prioritise:

Elements not tested in the longest time.

Elements re-set or modified since last test.

Elements that operated in service since last test.

At least one critical element per visit (e.g. 87G, 40).

Avoid testing only the easy elements; alternate to give all elements a turn.

## 6.3 Element Tracker — Last Tested / This Visit Selection

| ANSI | ABB Function | Description | Enabled? (Y/N) | Last tested (date) | Test this visit? (Y/N) | Result |
| --- | --- | --- | --- | --- | --- | --- |
| 87G | GENPDIF | Generator differential |  |  |  |  |
| 87T | T2WPDIF | Unit transformer differential |  |  |  |  |
| 87N | REFPDIF | Restricted earth fault (low-Z) |  |  |  |  |
| 64S | STTIPHIZ | 100% stator earth fault (20 Hz inj.) |  |  |  |  |
| 64R | ROTIPHIZ | Rotor earth fault (injection) |  |  |  |  |
| 40 | LEXPDIS | Loss of excitation (impedance) |  |  |  |  |
| 78 | PSPPPAM | Pole slip (lens characteristic) |  |  |  |  |
| 51V | VRPVOC | Volt-restrained overcurrent (stator backup) |  |  |  |  |
| 50/51 | OC4PTOC | Phase overcurrent backup |  |  |  |  |
| 50N/51N | EF4PTOC | Residual overcurrent backup |  |  |  |  |
| 46 | NS4PTOC | Negative-sequence overcurrent |  |  |  |  |
| 49S | GSPTTR | Stator thermal overload (I²t) |  |  |  |  |
| 49R | GRPTTR | Rotor thermal overload (I²t) |  |  |  |  |
| 27 | UV2PTUV | Undervoltage (2-step) |  |  |  |  |
| 59 | OV2PTOV | Overvoltage (2-step) |  |  |  |  |
| 59N | ROV2PTOV | Residual / zero-seq. overvoltage |  |  |  |  |
| 24 | OEXPVPH | Overexcitation (V/Hz) |  |  |  |  |
| 32 | GOPPDOP | Directional overpower / reverse power |  |  |  |  |
| 37 | GUPPDUP | Directional underpower |  |  |  |  |
| 50BF | CCRBRF | Breaker failure (3-phase) |  |  |  |  |
| 52PD | CCPDSC | CB pole discrepancy |  |  |  |  |
| 25 | SESRSYN | Synchronism / energising check |  |  |  |  |
| 50AE | AEGPVOC | Accidental / inadvertent energising |  |  |  |  |
| 81U | SAPTUF | Underfrequency |  |  |  |  |
| 81O | SAPTOF | Overfrequency |  |  |  |  |
| 81R | SAPFRC | Rate of change of frequency (ROCOF) |  |  |  |  |
| 60 | FUFSPVC | Fuse / VT failure supervision |  |  |  |  |
| CCS | CCS | Current circuit supervision |  |  |  |  |

## 6.4 Per-Element Test Result Template

Copy this template into the test record for each element tested in this visit.

| Element / ANSI |  |
| --- | --- |
| ABB function (IEC 61850 ID) |  |
| Setting tested (pickup / reach / curve) |  |
| Pickup setting |  |
| Pickup measured |  |
| Pickup error % |  |
| Time delay setting (s) |  |
| Time measured (s) |  |
| Time error % |  |
| Result | ☐ PASS ☐ FAIL |

# 7. Post-Test Checks

## 7.1 Re-compare Settings to Master

☐  Read settings from the IED again after element testing complete (PCM600 upload).

☐  Save the PCM600 project as: asleft_[date]_[IED tag].pcm.

☐  Compare as-left against the approved master settings.

☐  Confirm zero unintended differences (only authorised changes, if any, remain).

☐  Confirm any temporarily disabled / modified functions have been restored.

| As-left project file name |  |
| --- | --- |
| Compare result vs. master | ☐ Identical ☐ Authorised changes only ☐ Differences (raise finding) |

## 7.2 Clear Events / Reset Targets

☐  Clear test-mode alarms via LHMI → Clear.

☐  Reset LHMI alarm LEDs and any latched indications.

☐  Confirm Internal events / disturbance buffers reviewed and archived as required.

## 7.3 Time Synchronisation Check

☐  Re-read IED date/time (Diagnostics → IED status → General).

☐  If drift was outside tolerance, correct via the configured time source.

☐  Confirm time synchronisation healthy: TIMESYNCHERROR inactive.

☐  Re-read time and confirm within tolerance of reference.

| Time source | ☐ GPS ☐ IRIG-B ☐ SNTP ☐ LON ☐ SPA ☐ BIN |
| --- | --- |
| Final IED time vs reference |  |

## 7.4 Restore Plant

☐  Disconnect all test leads from IED terminals.

☐  Replace all test block links / reinstate VT MCBs.

☐  Remove CT shorting links and confirm CT secondary continuity through to source.

☐  Restore trip and lockout output links / re-enable trips.

☐  Confirm the self-supervision “Normal” (green) LED is re-lit and steady after test completion.

☐  Clear any remaining test-mode alarms via LHMI → Clear.

☐  Verify the INTERNAL FAIL contact on the PSM is de-energised (healthy).

☐  Confirm the active setting group is restored to the correct group (NOT left in a test group).

☐  Confirm 64S / 64R injection systems (REX060 units) are re-enabled if blocked for testing.

☐  Verify no targets / alarm LEDs remain active on the IED or panel.

☐  Confirm SCADA / DCS analogue values match IED metering (live readings, post-restoration).

☐  Re-energise VTs; observe sensible secondary voltages on the IED before declaring complete.

☐  Operations / control room notified that work is complete.

☐  Permit returned and isolations removed (LOTO removed).

## 7.5 Final Self-Supervision Check

☐  Confirm Main menu → Diagnostics → IED status → General reports no FAIL or WARNING.

☐  Confirm the “Normal” green LED is lit and steady.

☐  Confirm the IED is in service / not in test mode per plant requirements.

☐  Capture final screenshots of IED status / Measurements / LED pages for the record.

# 8. Findings, Defects & Recommendations

Use this log to record every individual finding raised during the test. The cover-page summary should reference these items.

| # | Finding / Defect | Severity | Action / NCR raised | Closed? |
| --- | --- | --- | --- | --- |

# 9. Test Files Index

Record full file paths / network locations for all data captured during the test.

| File type | File name | Location | Initials |
| --- | --- | --- | --- |
| Events (EVE) |  |  |  |
| Disturbance records (DRPRDRE) |  |  |  |
| Internal events list |  |  |  |
| As-found PCM600 project |  |  |  |
| As-left PCM600 project |  |  |  |
| Omicron test file (.occ) |  |  |  |
| Screenshots |  |  |  |

# 10. Test Sign-Off

By signing below, the tester and witness confirm that all activities recorded above were performed and the results are accurate.

| Tester name |  |
| --- | --- |
| Tester signature |  |
| Date |  |
| Witness name |  |
| Witness signature |  |
| Date |  |
| Authorising engineer (acceptance) |  |
| Signature |  |
| Date |  |
| Overall test result | ☐ PASS ☐ PASS with defects ☐ FAIL |