## 1. Cover
PROTECTION RELAY TEST RESULTS
ABB Relion REG670 2.0 (ANSI) Generator Protection IED — Live Results Template
Test Summary & Findings (filled in at end of visit)
Overall outcome
Test completion date
Summary & Findings
Self-supervision status on departure
Test Information
Site / Power station
Asset identifier (generator / unit)
Work order / Job number
Reason for test | Routine
Test date (start)
Test date (finish)
Personnel
Tester (name)
Tester signature
Witness / 2nd person
Witness signature
Authorising engineer
IED Under Test
IED model | ABB Relion REG670 2.0 (ANSI)
IED tag / functional ID
Serial number (SerialNo)
Ordering number (OrderingNo)
Firmware version (FirmwareVer)
Product version (ProductVer)
Production date (ProductionDate)
Panel / cubicle location
Active setting group (GRP 1–6)
Global base voltage VBase (kV)
Global base current IBase (A)
PCM600 project file name
Notes
CT / VT Ratios (primary : secondary) — drives Expected Primary in analogue tables
Ratio | Primary | Secondary | Ratio (P/S) | Unit
Main VT (line-N) | 11000 | 63.5 |  | V
Neutral VT (VN) | 11000 | 110 |  | V
Generator terminal CT | 1000 | 5 |  | A
Generator neutral CT | 1000 | 5 |  | A
Test Tolerances (drives auto pass/fail)
Voltage magnitude tolerance (%) | 1
Current magnitude tolerance (%) | 1
Phase angle tolerance (°) | 1
Element pickup tolerance (%) | 5
Element timing tolerance (%) | 5
Auto-rolled-up status (calculated)
Analogue inputs
Element tests
Auto overall
Legend: blue text = user input. Grey/auto cells are calculated. Yellow tolerance cells drive PASS/FAIL.

## 2. Equip & Refs
Test Equipment & Reference Drawings
Equipment | Make / Model | Serial No. | Last Cal. | Cal. Due
Three-phase test set | Omicron CMC
Laptop (PCM600)
20 Hz injection set (64S/64R) | ABB REX060
Drawing No. | Title | Revision | Date
Single line diagram
AC schematic / CT-VT
DC schematic / trip
Binary I/O allocation
Test File & Reference Document Locations
Omicron test file (.occ)
PCM600 project file (.pcmp/.pcmi)
SharePoint — Settings
SharePoint — Functional description
SharePoint — Drawings

## 3. Pre-Test
Pre-Test Checklist
3.1 Visual Inspection
# | Check | Status | Notes / Value | Initials
1 | IED mounted securely; no physical damage to LHMI or terminals.
2 | LHMI display, buttons and LEDs illuminate during lamp test.
3 | All wiring terminations tight (sample); no overheating.
4 | No active alarm LEDs or messages on arrival.
5 | Aux supply at PSM within tolerance (record value).
6 | INTERNAL FAIL contact wiring on PSM intact.
3.2 Connect to IED & Verify Status
# | Check | Status | Notes / Value | Initials
7 | Connected via LHMI (front RJ-45) or PCM600 (Ethernet).
8 | "Normal" green status LED lit and steady (IED healthy).
9 | Diagnostics > IED status > General: no FAIL/WARNING active.
10 | Firmware version recorded from Product identifiers (Cover).
11 | Firmware matches plant register.
3.3 Self-Supervision Review (ABB-specific)
# | Check | Status | Notes / Value | Initials
12 | Diagnostics > Internal events reviewed; events since last visit recorded.
13 | No active FAIL / WARNING / RTCERROR / TIMESYNCHERROR signals.
14 | No RTEERROR / IEC61850ERROR / WATCHDOG / LMDERROR / APPERROR.
15 | No module errors (PSM/ADOne/BIM/BOM/IOM/MIM/LDCM).
16 | INTERNAL FAIL contact on PSM de-energised (healthy).
17 | No self-supervision alarm LEDs lit.
18 | Overall self-supervision status recorded (All OK / events noted).
3.4 Time / Clock Check
# | Check | Status | Notes / Value | Initials
19 | Read IED date/time (Diagnostics > IED status > General); record drift.
20 | Time source identified (GPS / IRIG-B / SNTP / LON / SPA / BIN).
21 | TIMESYNCHERROR signal state noted.
3.5 Event & Disturbance Records
# | Check | Status | Notes / Value | Initials
22 | Events exported (LHMI > Events / PCM600) as YYYYMMDD_[tag]_EVE_asfound.
23 | Disturbance records (DRPRDRE) downloaded as YYYYMMDD_[tag]_DIST_asfound.
24 | Reviewed for unexpected operations / pickups / chatter.
25 | Anomalies cross-referenced with operations / SCADA log.
3.6 Settings — As-Found
# | Check | Status | Notes / Value | Initials
26 | PCM600 upload; saved as asfound_[date]_[tag].pcm.
27 | Compared as-found vs. master settings.
28 | All differences documented.
29 | Differences are authorised changes only.
3.7 Settings vs. Functional Description
# | Check | Status | Notes / Value | Initials
30 | Enabled functions match functional description.
31 | Key element settings match document.
32 | CT/VT ratios and VBase/IBase match nameplate/SLD and Cover.
33 | Trip matrix / SMBO output mapping matches functional description.
34 | Active setting group recorded.

## 4. Analogue Inputs
Analogue Input Verification — PRIMARY values
Inject secondary; the IED reports PRIMARY values via Measurements using the ratios on the Cover. Expected Primary, error % and pass/fail compute automatically. Magnitude tolerance: TolV_pct / TolI_pct; angle tolerance: TolAngle_deg.
If Expected Primary is blank, check the corresponding CT/VT ratio is filled on the Cover.
4.1 Main VT — Three-Phase Voltage Injection
Step | Injected (sec) | Inj Angle (°) | Phase / Input | Expected Primary | Relay Primary Reported | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 63.5 | 0 | L1 (VA)
1 | 63.5 | -120 | L2 (VB)
1 | 63.5 | 120 | L3 (VC)
2 | 30 | 0 | L1 (VA)
2 | 30 | -120 | L2 (VB)
2 | 30 | 120 | L3 (VC)
4.2 Neutral VT — Generator Neutral Voltage (VN)
Step | Injected (sec) | Inj Angle (°) | Phase / Input | Expected Primary | Relay Primary Reported | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 10 | 0 | VN
2 | 30 | 0 | VN
3 | 60 | 0 | VN
4 | 100 | 0 | VN
4.3 Generator Terminal CT — Three-Phase Current Injection
Step | Injected (sec) | Inj Angle (°) | Phase / Input | Expected Primary | Relay Primary Reported | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 1 | 0 | L1 terminal
1 | 1 | -120 | L2 terminal
1 | 1 | 120 | L3 terminal
2 | 5 | 0 | L1 terminal
2 | 5 | -120 | L2 terminal
2 | 5 | 120 | L3 terminal
4.4 Generator Neutral CT — Three-Phase Current Injection
Step | Injected (sec) | Inj Angle (°) | Phase / Input | Expected Primary | Relay Primary Reported | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 1 | 0 | L1 neutral
1 | 1 | -120 | L2 neutral
1 | 1 | 120 | L3 neutral
2 | 5 | 0 | L1 neutral
2 | 5 | -120 | L2 neutral
2 | 5 | 120 | L3 neutral
4.5 87G Differential Stability (Through-Current Injection)
Phase | Terminal I (A pri) | Neutral I (A pri) | Id operating (A) | Ibias (A)
L1
L2
L3

## 5. Binary IO
Binary Input / Output Functional Tests (SMBI / SMBO)
5.1 Binary Inputs (SMBI)
Input | Description / Source | Pickup V (V) | Asserted? (Y/N) | Event captured? (Y/N) | Status | Notes | Initials
BI01 | 86G lockout relay asserted
BI02 | Plant available / off-line
BI03 | Generator breaker open
BI04 | Exciter breaker open
BI05 | Test mode enable
BI06 | REF695 block (if applied)
BI07
BI08
5.2 Binary Outputs (SMBO)
Output | Driven by / Function | Force method | Continuity (Y/N) | Operates target (Y/N) | Status | Notes | Initials
BO01 | Trip Generator Breaker | PCM600 force
BO02 | Trip Exciter Breaker (40) | PCM600 force
BO03 | Trip & Lockout 86G | PCM600 force
BO04 | Alarm | PCM600 force
BO05 | INTERNAL FAIL (INTERRSIG FAIL) | PCM600 force
BO06 |  | PCM600 force
BO07 |  | PCM600 force
BO08 |  | PCM600 force

## 6. Element Tracker
Protection Element Tracker
ANSI | ABB Function | IEC 61850 ID | Description | Enabled? (Y/N) | Last tested (date) | Test this visit? (Y/N) | Result | Notes
87G | GENPDIF | GENPDIF | Generator differential
87T | T2WPDIF | T2WPDIF | Unit transformer differential
87N | REFPDIF | REFPDIF | Restricted earth fault (low-Z)
64S | STTIPHIZ | STTIPHIZ | 100% stator earth fault (20 Hz inj.)
64R | ROTIPHIZ | ROTIPHIZ | Rotor earth fault (injection)
40 | LEXPDIS | LEXPDIS | Loss of excitation (impedance)
78 | PSPPPAM | PSPPPAM | Pole slip (lens)
51V | VRPVOC | VRPVOC | Volt-restrained OC (stator backup)
50/51 | OC4PTOC | OC4PTOC | Phase overcurrent backup
50N/51N | EF4PTOC | EF4PTOC | Residual overcurrent backup
46 | NS4PTOC | NS4PTOC | Negative-sequence overcurrent
49S | GSPTTR | GSPTTR | Stator thermal overload (I²t)
49R | GRPTTR | GRPTTR | Rotor thermal overload (I²t)
27 | UV2PTUV | UV2PTUV | Undervoltage (2-step)
59 | OV2PTOV | OV2PTOV | Overvoltage (2-step)
59N | ROV2PTOV | ROV2PTOV | Residual overvoltage
24 | OEXPVPH | OEXPVPH | Overexcitation (V/Hz)
32 | GOPPDOP | GOPPDOP | Directional overpower
37 | GUPPDUP | GUPPDUP | Directional underpower
50BF | CCRBRF | CCRBRF | Breaker failure (3-phase)
52PD | CCPDSC | CCPDSC | CB pole discrepancy
25 | SESRSYN | SESRSYN | Synchronism / energising check
50AE | AEGPVOC | AEGPVOC | Accidental energising
81U | SAPTUF | SAPTUF | Underfrequency
81O | SAPTOF | SAPTOF | Overfrequency
81R | SAPFRC | SAPFRC | ROCOF
60 | FUFSPVC | FUFSPVC | Fuse / VT failure supervision
CCS | CCS | CCS | Current circuit supervision

## 7. Element Results
Per-Element Test Results
# | ANSI | ABB Function | Setting tested | Pickup setting | Pickup measured | Pickup err % | Time setting (s) | Time measured (s) | Time err % | Result | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16

## 8. Post-Test
Post-Test Checklist
8.1 Settings re-comparison (as-left vs. master)
# | Check | Status | Notes / Value | Initials
1 | PCM600 upload; saved as asleft_[date]_[tag].pcm.
2 | Compared as-left vs. master settings.
3 | Zero unauthorised differences remain.
4 | Temporarily disabled / modified functions restored.
8.2 Clear alarms / reset indications
# | Check | Status | Notes / Value | Initials
5 | Test-mode alarms cleared via LHMI > Clear.
6 | LHMI alarm LEDs and latched indications reset.
7 | Internal events / disturbance buffers reviewed and archived.
8.3 Time synchronisation
# | Check | Status | Notes / Value | Initials
8 | Re-read IED date/time.
9 | If drift outside tolerance, corrected via configured time source.
10 | TIMESYNCHERROR inactive; sync healthy.
11 | Final drift within tolerance.
8.4 Plant restoration (REG670-specific)
# | Check | Status | Notes / Value | Initials
12 | Disconnected all test leads from IED terminals.
13 | Replaced all test block links / reinstated VT MCBs.
14 | Removed CT shorting links; verified continuity to source.
15 | Restored trip and lockout output links / re-enabled trips.
16 | Self-supervision "Normal" green LED re-lit and steady.
17 | Cleared any test-mode alarms via LHMI > Clear.
18 | INTERNAL FAIL contact de-energised (healthy).
19 | Active setting group restored to correct group (not test group).
20 | 64S/64R injection systems (REX060) re-enabled if blocked.
21 | No targets / alarm LEDs remain active on IED or panel.
22 | SCADA / DCS analogue values match IED metering live.
23 | Re-energised VTs; sensible secondary voltages on IED.
24 | Operations / control room notified work complete.
25 | Permit returned and isolations removed (LOTO removed).
8.5 Final self-supervision check
# | Check | Status | Notes / Value | Initials
26 | Diagnostics > IED status > General: no FAIL / WARNING.
27 | "Normal" green LED lit and steady.
28 | IED in service / not in test mode per plant requirements.
29 | Final screenshots captured (status / Measurements / LEDs).

## 9. Files & Sign-Off
Findings Log & Sign-Off
Findings, Defects & Recommendations (detailed log)
# | Finding / Defect | Severity | Closed?
1
2
3
4
5
6
7
8
Test Files Index
File type | File name | Location
Events (EVE)
Disturbance records (DRPRDRE)
Internal events list
As-found PCM600 project
As-left PCM600 project
Omicron test file (.occ)
Screenshots
Sign-Off
Tester name
Tester signature
Date
Witness name
Witness signature
Date
Authorising engineer (acceptance)
Signature
Date
Overall test result (from Cover sheet)