## 0. Instructions
NEW RELAY ONBOARDING FORM
Fill in once per new relay type. Hand the completed form back to the protection-systems lead (or an LLM assistant) to generate the standard check sheet + results template pair.
How to use this form
1. Work through tabs 1 → 6 in order. Each tab has a brief context note at the top.
2. Cells with a PINK background are required. Cells with a WHITE background are optional but recommended.
3. Blue text in any cell = your input. Default values are placeholders to overwrite — adjust to match the actual relay.
4. Drop-downs are used where there is a fixed set of valid answers (e.g. Yes/No, function class).
5. When complete, save the file with a meaningful name (e.g. "Onboarding_SEL-411L.xlsx") and hand it to the documentation generator.
6. Reference document: "Protection Relay Test Documentation — Standard Specification.docx" describes the full pattern. Read it for context if you've not seen it before.
What you'll need before starting
• Relay nameplate / part-number details (model, FID expectations, port layout).
• Protection Functional Description / Protection Report for an example installation of this relay type.
• Default CT and VT ratios that are typical for the asset class (e.g. transmission line CTs are usually different from generator CTs).
• A clear understanding of any non-standard protection schemes used (line differential, communications-aided tripping, etc.).
Output you'll get back
• <Relay>_Test_Check_Sheet.docx — printable / fillable procedure document.
• <Relay>_Test_Results_Template.xlsx — live workbook with auto pass/fail calculations.
• Both files match the structure described in the Standard Specification, customised with the inputs you provide here.

## 1. Relay Identity
1. Relay Identity
Basic information about the relay model and its protection role.
Relay model & function
Relay model (short code) | SEL387
Full subtitle / description (cover banner) | SEL387 Differential Protection
Primary asset class | Transformer
Filename prefix (for output documents) | SEL-387
Manufacturer | SEL
Typical site application | Transformer Protection
Communications & special schemes
Line differential (87L) — relay uses fibre to remote terminal?
Communications-aided tripping (POTT / DCB / DCUB) used?
Auto-reclose (79) typically enabled?
Synch-check (25) typically enabled?
Breaker arrangement common to this class | LV and HV Breaker

## 2. Analogue Inputs
2. Analogue Inputs
Which VT and CT inputs the relay has, and their default ratios.
List every analogue input that the relay measures, with a sensible default primary and secondary value for the template. These drive the Cover sheet's CT/VT ratio block and the per-section analogue tables in section 4.
Analogue inputs inventory
Input name | Type | Default Primary | Default Secondary | Unit | Notes (location, polarity, etc.)
Main VT (line-N) | VT (3-phase) | 132000 | 63.5 | V | Primary VT, used for distance and metering
Sync VT | VT (single-phase) | 132000 | 63.5 | V | Used by 25 sync-check
Line CT | CT (3-phase) | 600 | 1 | A | Single CT set (single breaker)
Section 4 sub-section structure to use
Most relays group inputs into 3–5 sub-sections (e.g. 4.1 three-phase voltage, 4.2 neutral voltage, 4.3 stator CT three-phase). Map each input above to a sub-section number below.
Sub-section | Title | Maps to input(s) above | Special check (stability / loopback)
4.1 | VT Inputs — Three-Phase Voltage Injection | Main VT
4.2 | Neutral / Synchronising Voltage Input | Sync VT (or Neutral VT)
4.3 | CT Inputs — Three-Phase Current Injection | Line CT
4.4 | Communications channel / stability check | All current inputs | Examples: 87L channel BER, 87G through-current sum ≈ 0, 87T balance
4.5

## 3. Protection Elements
3. Protection Elements
ANSI list to populate the element tracker in Section 6.3 of the check sheet.
List every protection function the relay class commonly implements. Up to 30 rows. Mark critical elements that should always feature in test rotation.
Element list
ANSI | Function description | Critical? (Y/N) | Default test priority | Notes
87L | Line current differential (Alpha plane) | Y | Every visit
21P Z1 | Phase distance Zone 1 | Y | Every visit | Trip zone
21P Z2 | Phase distance Zone 2 | N | Annual
21P Z3+ | Phase distance Zone 3+ | N | 2-yearly
21G Z1 | Ground distance Zone 1 | Y | Every visit
21G Z2 | Ground distance Zone 2 | N | Annual
50/51 | Phase overcurrent / inverse-time | N | Annual
50N/51N | Residual / neutral overcurrent | N | Annual
67 | Directional overcurrent | N | Annual
50BF | Breaker failure | Y | Every visit
27 | Undervoltage | N | 2-yearly
59 | Overvoltage | N | 2-yearly
81 O | Over-frequency | N | Annual
81 U | Under-frequency | N | Annual
25 | Synchronism check | N | Annual
79 | Auto-reclose | N | Annual
60 | VT supervision / LOP | N | Annual
78 | Out-of-step / power-swing | N | 2-yearly
POTT/DCB | Communications-aided tripping | Y | Every visit

## 4. Binary IO Defaults
4. Binary I/O Defaults
Default function labels for the binary input and output rows. Tester adjusts per site.
Pre-fill the typical function each binary input/output drives for this relay class. These appear in the "Function" column of section 5 in the check sheet and tab 5 in the results template. Tester can adjust per actual site wiring.
Binary inputs — default sources
Input | Default description / source
IN101 | Circuit breaker 52a (closed) status
IN102 | Circuit breaker 52b (open) status
IN103 | Trip from external scheme (e.g. busbar protection)
IN104
IN105
IN106
IN201
IN202
Binary outputs — default driven functions
Output | Default driven by / function
OUT101 | Trip (line breaker)
OUT102 | Reclose
OUT103 | POTT / DCB key TX
OUT104 | Alarm
OUT105
OUT201
OUT202
OUT203

## 5. Custom Checklists
5. Custom Checklists
Relay-specific items to add to safety + post-test checklists.
Add any relay-specific checks that should appear in section 2 (Safety, before testing) or section 7.4 (Plant restoration, after testing). Leave blank if the standard checklist is sufficient.
Additional pre-test / safety checks (Section 2)
# | Check item | Required?
1 | Block 87L / 87G / 87T scheme before injecting (will produce operating quantity). | Yes
2 | Disable auto-recloser (79) at relay or scheme level. | Yes
3 | Inhibit POTT / DCB / DCUB transmission to remote end. | Yes
4 | Notify remote-end personnel before end-to-end testing. | Yes
5
6
Additional post-test / restoration checks (Section 7.4)
# | Check item | Required?
1 | Re-enable auto-recloser (79) at relay or scheme level. | Yes
2 | Re-instate 87L / 87G / 87T scheme — coordinate with remote end where applicable. | Yes
3 | Re-enable POTT / DCB / DCUB transmission. | Yes
4 | Confirm 87L channel reports CHOK at both ends. | Yes
5
6

## 6. Output & Submit
6. Output & Submission
Where the generated documents will live.
Naming & storage
Output filename prefix (matches tab 1) | SEL-411L
Target SharePoint folder URL | https://sharepoint.contactenergy.co.nz/
Owner / Lead protection engineer
Form completed by
Date completed
Review status | Draft
Submission checklist (verify before handing back)
☐ | Tab 1 (Relay Identity) — every field populated
☐ | Tab 2 (Analogue Inputs) — every input listed, ratios sensible, sub-sections mapped
☐ | Tab 3 (Protection Elements) — at least 12 elements listed, critical ones marked
☐ | Tab 4 (Binary I/O Defaults) — function defaults reviewed (or accepted as standard)
☐ | Tab 5 (Custom Checklists) — any relay-specific safety / restoration items added
☐ | Tab 6 (this tab) — naming and storage location confirmed