PROTECTION RELAY TEST DOCUMENTATION

Standard Specification & Design Pattern

Pattern for creating routine-test check sheets and live results templates for any SEL protection relay.

## Document Control

| Revision | Date | Description | Prepared By | Approved By |
| --- | --- | --- | --- | --- |
| 1.0 |  | Initial issue | Michael du Plessis |  |

# 1. Purpose & Scope

This specification describes the standard documentation pattern used for routine and maintenance testing of SEL protection relays. It captures the structure, conventions, formula architecture and content of two paired deliverables:

- A check sheet (.docx) — the procedure followed during the test visit and the form filled in with results, observations and sign-off.

- A live results template (.xlsx) — a structured workbook that captures the same data digitally, with auto pass/fail calculation against configurable tolerances and a rolled-up overall outcome.

The pattern is relay-agnostic. Two reference implementations exist:

- SEL-300G — generator protection relay (worked example throughout this document).

- SEL-311L — line current differential & distance relay (worked example).

To apply the pattern to a new relay (e.g. SEL-411L, SEL-487E, SEL-700G), fill in the companion New Relay Onboarding Form (.xlsx) and use this document as the structural reference.

# 2. Document Set & Deliverables

For each relay in service, the standard package is:

| File | Type | Purpose | Filled in by |
| --- | --- | --- | --- |
| <Relay>_Test_Check_Sheet.docx | .docx | Step-by-step test procedure; printed or filled in electronically. Captures targets, findings and sign-off. | Tester |
| <Relay>_Test_Results_Template.xlsx | .xlsx | Live workbook capturing measured values; auto-calculates pass/fail against tolerances; rolls up overall outcome. | Tester |
| Protection Relay Test Documentation — Specification.docx | .docx | This document. Defines the standard structure and conventions. | Lead protection engineer |
| New Relay Onboarding Form.xlsx | .xlsx | Intake form filled in once per relay type to drive generation of a new check sheet + results template pair. | Lead protection engineer |

# 3. Common Conventions

## 3.1 Branding

| Logo | Contact logo, embedded in both deliverables. Appears centred on the cover page (6 cm wide) and at the top-left of every page header (small). |
| --- | --- |
| Brand colour | #1F4E79 (deep blue) — used for section headers, h1 fills, table header rows. |
| Accent colour | #D9E2F3 (light blue) — used for label cells in info tables. |
| Note background | #FFF2CC (warm yellow) — used for caution/note callouts and tolerance input cells. |
| Summary background | #FFF8E7 (cream) — used for free-text summary/findings boxes. |
| PASS colour pair | Fill #C6EFCE / text #006100 |
| FAIL colour pair | Fill #FFC7CE / text #9C0006 |

## 3.2 Layout

| Page size | A4 portrait (210 × 297 mm), 1 cm margins |
| --- | --- |
| Font | Calibri (default for docx-js / openpyxl) |
| Body size | 11 pt (size 22 in docx-js half-points; size 10 in openpyxl) |
| Header h1 | 14 pt bold, white text on brand-blue fill |
| Header h2 | 12 pt bold, brand-blue text, brand-blue underline |
| Header h3 | 11 pt bold, dark grey |
| Page header | Logo (1.8 cm wide) + document title (left), Asset field (right). Repeats on every page. |
| Page footer | Doc Rev (left), "Page X of Y" (right). Repeats on every page. |

## 3.3 User-Input Convention (xlsx)

- Blue text (RGB 0,0,255) in any cell = field intended for user input.

- Black bold text on grey/alt-row background = auto-calculated cell. Tester does not edit.

- Yellow-filled cell = tolerance / configurable setting. Editable but treat as a setting, not data.

- Header rows in brand blue with white text = column headers; do not edit.

## 3.4 Status Colour-Coding (xlsx)

Conditional formatting applied to status / Pass-Fail columns throughout:

- Cell value "PASS" → green fill, dark green bold text.

- Cell value "FAIL" → red fill, dark red bold text.

- Cell value "OK" (pre-test / post-test checklists) → green fill.

- Empty or any other value → unstyled (default cell).

# 4. Check Sheet (.docx) Structure

Every check sheet follows the same section order. Sections in bold below are relay-agnostic (identical wording across all relays). Sections marked [VARIES] customise per relay.

## 4.1 Cover & Front Matter

| Block | Content | Varies per relay? |
| --- | --- | --- |
| Cover banner | Contact logo (centered, 6 cm). Title "PROTECTION RELAY TEST CHECK SHEET". Subtitle = relay model and protection function. Strapline "Routine / Maintenance Test Procedure". | Subtitle only |
| Document Control | Revision, Date, Description, Prepared By, Approved By. 1 issued row + 2 blank. | No |
| Test Summary & Findings | Cream-shaded block: Overall outcome (3 checkboxes), Test completion date, large free-text Summary & Findings area. Filled in by tester at end of visit. | No |

## 4.2 Section 1 — Test Information

| Sub-section | Fields | Varies per relay? |
| --- | --- | --- |
| 1.1 Site & Project | Site, Asset identifier, Work order, Reason for test (checkbox row), Test dates start/finish. | No |
| 1.2 Personnel | Tester, signature, Witness, signature, Authorising engineer. | No |
| 1.3 Relay Under Test | Relay model, Relay tag/ID, Serial, FID, Part number, Panel location, Settings group, CT and VT ratios (rows depend on relay's analogue inputs). | [VARIES] — ratio rows |
| 1.4 Test Equipment | Equipment, Make/Model, Serial No, Last Cal date, Cal Due. 4 prefilled rows. | No |
| 1.5 Reference Drawings | Drawing No, Title, Revision, Date. Pre-labelled with SLD, schematics AC/DC, panel GA. 6 rows. | No |
| 1.6 Test File & Document Locations | Omicron .occ filename + 4 SharePoint hyperlink fields (Settings, Test file, Functional Report, Other). | No |

## 4.3 Section 2 — Safety, Isolations & Permits

Standard checklist (~11 items) plus an Isolation Record table (5 cols × 6 rows). Items may be added at the bottom for relay-specific blocking (e.g. "Block 87L scheme", "Disable auto-recloser").

[VARIES] — append relay-specific blocking checks for differential schemes, recloser, communications-aided tripping.

## 4.4 Section 3 — Pre-Test Checks (7 sub-sections, standard)

| Sub-section | Purpose |
| --- | --- |
| 3.1 Visual Inspection | Physical state of relay, terminals, wiring, LEDs, aux supply. |
| 3.2 Connect to Relay & Verify Status | Establish comms, STATUS / MET commands, FID match plant register. |
| 3.3 Time / Clock Check | Drift vs reference; flag for correction at end of test. |
| 3.4 Download Event Records | HIS/EVE export, file naming convention, anomaly review. |
| 3.5 Download Sequence of Events (SOE) | SER export, review for unexpected pickups or input chatter. |
| 3.6 Settings — As-Found | Read settings, save with "asfound_" prefix, compare against master file. |
| 3.7 Settings vs. Protection Functional Description | Verify enabled functions + key settings align with the approved Functional Description. |

## 4.5 Section 4 — Analogue Input Verification (PRIMARY values)

This is the core measurement section and the most heavily customised per relay.

Design principle: the relay scales the secondary signal it receives internally using the configured CT/VT ratios. The check sheet verifies the relay reports the correct PRIMARY value — not the secondary value. This catches ratio-setting errors that simple secondary checks would miss.

Standard table columns for every analogue injection:

- Step (1, 2, 3 …)

- Injected magnitude (V secondary or A secondary — what the test set produces)

- Injected angle (°)

- Phase / Input label (e.g. L1 (VA))

- Expected Primary (V/kV or A) — calculated by tester as injected × ratio

- Relay Primary value reported

- Relay angle reported

- Error % (magnitude)

- Pass / Fail

NOTE: In the xlsx, columns 5 (Expected Primary) and 8 (Error %) are auto-calculated formulas; the Pass/Fail column uses the magnitude and angle tolerances on the Cover sheet.

[VARIES] — each relay defines its own sub-sections within Section 4:

| Sub-section | Worked example: SEL-300G | Worked example: SEL-311L |
| --- | --- | --- |
| 4.1 — three-phase voltage | Main VT inputs (L1/L2/L3) | Line VT inputs (L1/L2/L3) |
| 4.2 — neutral / synchronising voltage | VN / 3V0 (broken-delta or generator neutral) | VS (synchronising voltage, single-phase) |
| 4.3 — three-phase current set 1 | Stator-side CTs (terminal end of generator) | Line CT inputs |
| 4.4 — three-phase current set 2 | Neutral-side CTs (machine end of generator, used by 87G) | — (single-breaker default; omitted) |
| 4.5 — stability/comms check | 87G through-current stability (sum of stator + neutral side ≈ 0) | 87L channel status, BER, propagation delay, end-to-end through-current test |

## 4.6 Section 5 — Binary I/O Functional Tests

- 5.1 Relay Binary Inputs — 10-row table (Input, Description, Pickup voltage, Asserted? Y/N, SER captured? Y/N, Initials). Default labels IN101–IN106, IN201–IN202.

- 5.2 Relay Binary Outputs — 10-row table (Output, Driven by/Function, Pulse cmd, Continuity Y/N, Operates target Y/N, Initials). Default labels OUT101–OUT105, OUT201–OUT203.

[VARIES] — prefilled Function column varies (e.g. "Trip", "Reclose", "POTT/DCB key TX" for 311L; "Trip BKR", "86 lockout" for 300G).

## 4.7 Section 6 — Protection Element Testing (Omicron)

- 6.1 Test File Structure — folder-per-element convention in the Omicron .occ file.

- 6.2 Element Selection Strategy — rotation between visits, prioritisation of critical / least-recently-tested elements.

- 6.3 Element Tracker — 22-row table (ANSI, Function, Enabled?, Last tested, Test this visit?, Result). [VARIES] — element list is relay-specific.

- 6.4 Per-Element Test Result Template — copy/paste block for each tested element.

## 4.8 Section 7 — Post-Test Checks

- 7.1 Re-compare Settings to Master — read "asleft_", compare, confirm only authorised changes.

- 7.2 Clear Events / Reset Targets.

- 7.3 Time Synchronisation — set relay clock if drift was outside tolerance.

- 7.4 Restore Plant — 9–12 checklist items. [VARIES] — relay-specific restoration items (re-enable 79, reinstate 87L, etc.).

- 7.5 Final Self-Test — STATUS OK, capture final screenshots.

## 4.9 Sections 8–10 — Findings, Files Index, Sign-Off

- 8 — Findings, Defects & Recommendations: detailed defect log (5 cols × 6 rows). Distinct from the cover-page Summary.

- 9 — Test Files Index: file type / name / location / initials table for the 9 standard test artefacts.

- 10 — Test Sign-Off: tester, witness, authorising engineer (name, signature, date) + overall result row.

# 5. Results Template (.xlsx) Structure

Mirrors the check sheet across 9 tabs. Adds live formulas, auto pass/fail and roll-up to the cover sheet.

| Tab | Mirrors check sheet | Live calculation |
| --- | --- | --- |
| 1. Cover | Front matter + Test Information + Personnel + Relay Under Test | CT/VT ratios drive analogue formulas; tolerances drive pass/fail; auto-rolled-up status |
| 2. Equip & Refs | Test Equipment + Reference Drawings + Document Locations | Hyperlinks auto-clickable |
| 3. Pre-Test | Section 3 (all 7 sub-sections) | OK/FAIL conditional formatting |
| 4. Analogue Inputs | Section 4 with PRIMARY value verification | Expected Primary, Mag Err %, Angle Err°, P/F — all formulas |
| 5. Binary IO | Section 5 (inputs + outputs) | PASS/FAIL conditional formatting |
| 6. Element Tracker | Section 6.3 | PASS/FAIL conditional formatting |
| 7. Element Results | Section 6.4 (one row per element tested) | Pickup err %, Time err %, Result — formulas |
| 8. Post-Test | Section 7 (all 5 sub-sections) | OK/FAIL conditional formatting |
| 9. Files & Sign-Off | Sections 8 + 9 + 10 | Overall result pulled from Cover |

## 5.1 Formula Architecture

Three layers of formulas drive the auto pass/fail behaviour:

### Layer 1 — Defined names on the Cover sheet

Each ratio and tolerance is exposed as a workbook-scoped defined name so formulas elsewhere can reference it by readable name:

Ratio_VTmain      → '1. Cover'!$E$<row>   (= Primary / Secondary cell)

Ratio_CTstator    → '1. Cover'!$E$<row>

TolV_pct          → '1. Cover'!$C$<row>   (voltage magnitude tolerance %)

TolI_pct          → '1. Cover'!$C$<row>

TolAngle_deg      → '1. Cover'!$C$<row>

TolPickup_pct     → '1. Cover'!$C$<row>   (element pickup tolerance %)

TolTime_pct       → '1. Cover'!$C$<row>

### Layer 2 — Per-row formulas in section 4 tables

Each analogue table row has these formulas (assume row N, mode V or I):

Expected Primary  = injected_secondary × Ratio_<applicable>

= C{N} * Ratio_VTmain

Mag Err %         = (Relay Primary − Expected Primary) / Expected Primary × 100

= (G{N} − F{N}) / F{N} × 100

Angle Err °       = Relay Angle − Injected Angle

= H{N} − D{N}

P/F               = IF either error exceeds its tolerance → "FAIL" else "PASS"

= IF(OR(ABS(I{N}) > TolV_pct, ABS(J{N}) > TolAngle_deg), "FAIL", "PASS")

NOTE: All formulas are wrapped in IFERROR + blank-input guards so empty cells leave the calculated cells blank, not #DIV/0!.

### Layer 3 — Cover sheet roll-up

The Cover sheet has an "Auto-rolled-up status" block with three cells:

Analogue inputs  = IF(COUNTIF('4. Analogue Inputs'!K:K, "FAIL") > 0, "FAIL",

IF(COUNTIF(...,"PASS") > 0, "PASS", ""))

Element tests    = COUNTIF('7. Element Results'!L:L, "FAIL")  → analogous

Auto overall     = IF either is FAIL → "FAIL",

IF both are PASS → "PASS",

else "INCOMPLETE"

The signed-off Overall outcome on the Cover (manual dropdown PASS / PASS WITH NOTES / FAIL) is the authoritative result; the Auto overall is provided as a cross-check.

## 5.2 Print Setup

- Every sheet has fitToWidth = 1, fitToHeight = 0 (fit one page wide, multiple pages tall).

- Page margins: 0.3" left/right, 0.4" top/bottom.

- Cover sheet image: Contact logo anchored at cell B1, 200 px wide.

# 6. What Varies Per Relay (customisation points)

When applying this pattern to a new relay, exactly these items need to be defined. Everything else is reused verbatim.

| Customisation point | Description | Where it appears |
| --- | --- | --- |
| Relay model | Short identifier (e.g. "SEL-411L") | Header, footer, cover subtitle, settings group label |
| Subtitle / function description | Full descriptive name (e.g. "Line Current Differential Relay") | Cover banner |
| Analogue input inventory | Which VTs and CTs exist and how they're labelled (Main VT, Sync VT, Stator CT, Neutral CT, Line CT...) | Section 1.3 ratio rows, Section 4 sub-sections, Cover ratio block, Tab 4 analogue tables |
| Default secondary nominal | Typical VT secondary (63.5 V or 110 V), CT secondary (1 A or 5 A) | Section 4 prefilled injection magnitudes |
| Communications scheme (if any) | 87L fibre, POTT, DCB, DCUB — additional checks for channel STATUS, BER, end-to-end stability | New sub-section in Section 4 (e.g. 4.4 or 4.6) |
| Stability/differential check | If 87G/87T/87L exists, add through-current stability sub-section verifying sum ≈ 0 | Section 4 sub-section |
| Protection element list | ANSI codes + element names enabled on this relay class | Section 6.3 element tracker, related guidance text |
| Critical element examples | 1–2 representative critical elements for the relay class | Section 6.2 example text, Omicron folder naming guidance |
| Relay-specific safety items | Block 87L scheme, disable auto-recloser, etc. | Section 2 safety checklist |
| Relay-specific restoration items | Re-enable scheme, reinstate communications | Section 7.4 restore plant |
| Binary output prefilled functions | e.g. "Trip BKR1", "POTT TX key", "86 lockout" — function names used in OUT row defaults | Section 5.2 binary outputs table |

# 7. Worked Examples

How the customisation points apply to the two reference implementations.

## 7.1 SEL-300G — Generator Protection Relay

| Subtitle | SEL-300G Generator Protection Relay |
| --- | --- |
| Analogue inputs (4 ratio rows) | Main VT (L-N), Neutral VT (3V0), Stator-side CT, Neutral-side CT |
| Section 4 sub-sections | 4.1 VT three-phase, 4.2 VN, 4.3 Stator CT three-phase, 4.4 Neutral CT three-phase, 4.5 Through-current 87G stability |
| Default secondary nominal | VT secondary 63.5 V, CT secondary 5 A |
| Default primary nominal | VT primary 11000 V, CT primary 1000 A |
| Critical elements (suggested rotation) | 87G, 40, 24, 64S, 50BF |
| Element list (22 rows) | 87G, 87T, 64S, 59N, 64F, 40, 32, 46, 24, 27, 59, 81 O/U/R, 21, 50/51, 50N/51N, 49, 78, 60, 50BF, 25 |
| Safety additions | Disable trip & 86 lockout, block diff trips |
| Special sections | 87G through-current stability check (4.5) |

## 7.2 SEL-311L — Line Current Differential & Distance Relay

| Subtitle | SEL-311L Line Current Differential & Distance Relay |
| --- | --- |
| Analogue inputs (3 ratio rows) | Line VT (L-N), Sync VT, Line CT |
| Section 4 sub-sections | 4.1 Line VT three-phase, 4.2 Sync VT, 4.3 Line CT three-phase, 4.4 87L communications & end-to-end |
| Default secondary nominal | VT secondary 63.5 V, CT secondary 1 A |
| Default primary nominal | VT primary 132000 V, CT primary 600 A |
| Critical elements (suggested rotation) | 87L, 21P Z1, 21G Z1, 50BF, POTT/DCB |
| Element list (22 rows) | 87L, 21P Z1/Z2/Z3+, 21G Z1/Z2/Z3+, 50/51, 50N/51N, 50G/51G, 67, 50BF, 27, 59, 81 O/U/R, 25, 79, 60, 78, POTT/DCB |
| Safety additions | Block 87L scheme, disable 79 auto-recloser, block POTT/DCB transmission |
| Special sections | 87L channel verification (4.4): STATUS, BER, round-trip delay, errored seconds, loopback, end-to-end through-current stability |

# 8. Process for Adding a New Relay

To produce a check sheet + results template for a relay not yet covered:

- Open the New Relay Onboarding Form (.xlsx) — companion file to this specification.

- Fill in each tab. The form prompts for every customisation point listed in Section 6.

- Validate the form: every required field on the Relay Identity, Analogue Inputs, Protection Elements and Custom Sections tabs must be populated.

- Hand the completed form to the protection-systems lead (or to an LLM assistant) for generation of the document pair.

- Review the generated check sheet against this specification: confirm all sections present, customised content correct, page numbers and headers right.

- Test the results template: enter a couple of sample values to confirm formulas evaluate correctly and pass/fail conditional formatting fires as expected.

- Issue the package: store both files in the project SharePoint location alongside the Functional Description / Protection Report for that asset.

# 9. Maintenance & Revision Control

- This specification governs the structure of all relay test documents in the protection-systems portfolio.

- Any structural change (new section, removed section, renamed sub-section) must be reflected here first, then propagated to all relay document pairs.

- Cosmetic changes (brand colours, header text wording) can be applied directly to the relay document pairs and back-ported here in the next revision.

- Tolerance defaults (1% magnitude, 1° angle, 5% pickup, 5% timing) are recommendations only — each relay document pair allows site-specific tolerances to be set on the Cover sheet.