## 1. Cover
PROTECTION RELAY TEST RESULTS
ABB REM615 Motor Protection Relay — Live Results Template
Test Summary & Findings (filled in at end of visit)
Overall outcome
Test completion date
Summary & Findings
Test Information
Site / Substation
Asset identifier (feeder / motor / transformer)
Work order / Job number
Reason for test | Routine
Test date (start)
Test date (finish)
Personnel
Tester (name)
Tester signature
Witness / 2nd person
Witness signature
Authorising engineer
Relay Under Test
Relay model | REM615
Relay function | Motor Protection (Relion 615 series)
Relay tag / functional ID
Order code / part number
Serial number
Firmware version
Panel / cubicle location
IED name (in PCM600 project)
Active settings group
CT / VT Ratios (primary : secondary) — drives Expected Primary in analogue tables
Ratio | Primary | Secondary | Ratio (P/S) | Unit (V/A)
Phase CT (3-phase) | 200 | 1 | 200 | V or A
Earth-fault Io CT (core-balance) | 50 | 1 | 50 | V or A
Test Tolerances (drives auto pass/fail)
Voltage magnitude tolerance (%) | 1
Current magnitude tolerance (%) | 1
Phase angle tolerance (°) | 1
Element pickup tolerance (%) | 5
Element timing tolerance (%) | 5
Auto-rolled-up status (calculated)
Analogue inputs
Element tests
Auto overall | INCOMPLETE

## 2. Equip & Refs
Test Equipment, Drawings & Reference Documents
Test Equipment Used
Three-phase test set | Omicron CMC
Laptop / PCM600 |  | N/A | N/A | N/A | N/A
Multimeter
Reference Drawings
Drawing No. | Title | Revision | Date | Notes
Single line diagram
Schematic — protection AC
Schematic — protection DC / trip
Panel general arrangement
Application configuration drawing (PCM600)
Test File & Reference Document Locations
Note: paste the SharePoint URL into each cell. Excel will turn it into a clickable link automatically.
Omicron test file (.occ filename)
SharePoint — PCM600 project / settings files (URL) | https://sharepoint.contactenergy.co.nz/
SharePoint — Omicron electronic test file (URL) | https://sharepoint.contactenergy.co.nz/
SharePoint — Protection Functional Report (URL) | https://sharepoint.contactenergy.co.nz/
SharePoint — Other (events, disturbance records, COMTRADE) (URL) | https://sharepoint.contactenergy.co.nz/

## 3. Pre-Test
Pre-Test Checklist
3.1 Visual Inspection
# | Check | Status | Notes / Value | Initials
1 | Relay mounted securely; no physical damage to fascia or terminals.
2 | All wiring terminations tight (sample); no signs of overheating.
3 | Front-panel LCD, LEDs and pushbuttons all functional.
4 | No active alarms, IRF indication or trip LEDs on arrival.
5 | Aux supply voltage at relay terminals within tolerance (record in Notes).
3.2 Connect to Relay & Verify Status (via PCM600)
# | Check | Status | Notes / Value | Initials
6 | Open PCM600; connect to IED via front USB or rear Ethernet (IEC 61850 / FTP).
7 | IED status reads OK in PCM600 (no IRF, no failures).
8 | Measurements view in PCM600 shows sane analogue values for current operating state.
9 | IED type, order code and firmware version recorded on Cover sheet (match plant register).
10 | Self-supervision details captured (no warnings or service condition issues).
3.3 Time / Clock Check
# | Check | Status | Notes / Value | Initials
11 | Read IED date/time from PCM600 or HMI; record drift vs. reference (Notes).
12 | Time sync source identified (IRIG-B, SNTP/NTP, PTP, manual).
13 | Sync status reports healthy (where applicable).
3.4 Event Records
# | Check | Status | Notes / Value | Initials
14 | Read event records from IED via PCM600 (Disturbance Recorder).
15 | Disturbance records exported (COMTRADE) and saved to job folder.
16 | Reviewed event list for unexpected operations / pickups since last test.
17 | Cross-referenced anomalies with operations / SCADA / fault log.
3.5 Sequence of Events (Event recorder)
# | Check | Status | Notes / Value | Initials
18 | Event recorder list reviewed for unexpected element pickups or input bouncing.
19 | Communications-related events (channel loss, NTP loss, IRF) reviewed.
3.6 Settings — As-Found
# | Check | Status | Notes / Value | Initials
20 | Read parameter setting from IED via PCM600; save IED-specific .pcmi (or read whole project).
21 | Save with filename prefix "asfound_<Asset>_<YYYYMMDD>.pcmi".
22 | Compared as-found vs. approved master parameter setting.
23 | All differences documented (record compare report file name in Notes).
24 | Differences are authorised changes only.
3.7 Settings vs. Protection Functional Description
# | Check | Status | Notes / Value | Initials
25 | Enabled function blocks match functional description.
26 | Key element settings (pickup, time delay, characteristic) match document.
27 | CT and VT ratios in IED match nameplate / SLD and Cover sheet.
28 | Application configuration (trip matrix / logic) matches functional description.
29 | Binary input / output mapping matches functional description.

## 4. Analogue Inputs
Analogue Input Verification — PRIMARY values
Inject secondary; IED reports primary internally using configured ratios on Cover. Expected Primary, error % and pass/fail are calculated automatically. Magnitude tolerance: TolV_pct/TolI_pct, angle tolerance: TolAngle_deg.
If Expected Primary shows blank, check the corresponding CT/VT ratio is filled in on the Cover sheet.
4.1 Phase CT Inputs — Three-Phase Current Injection (Primary verification)
Step | Injected (A sec) | Inj Angle (°) | Phase / Input | Expected Primary (A) | Relay Primary | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 0.5 | 0 | L1 (IL1) | 100
1 | 0.5 | -120 | L2 (IL2) | 100
1 | 0.5 | 120 | L3 (IL3) | 100
2 | 1 | 0 | L1 (IL1) | 200
2 | 1 | -120 | L2 (IL2) | 200
2 | 1 | 120 | L3 (IL3) | 200
3 | 5 | 0 | L1 (IL1) | 1000
3 | 5 | -120 | L2 (IL2) | 1000
3 | 5 | 120 | L3 (IL3) | 1000
4.2 Earth-Fault Io Input — Single-Phase Current Injection (Primary verification)
Step | Injected (A sec) | Inj Angle (°) | Phase / Input | Expected Primary (A) | Relay Primary | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 0.05 | 0 | Io | 2.5
2 | 0.2 | 0 | Io | 10
3 | 1 | 0 | Io | 50

## 5. Binary IO
Binary Input / Output Functional Tests
5.1 Binary Inputs (BI)
Apply rated voltage to each binary input (or operate the source field device) and confirm the input asserts in PCM600 (Function blocks / Event recorder).
BI Channel | Description / Source | Pickup V (V) | Asserted? (Y/N) | Event captured? (Y/N) | Status | Notes | Initials
BI1 | Trip from external (e.g. BBP)
BI2 | Local/Remote selector
BI3 | Reset external
BI4 | Aux contact 52a (CB closed)
BI5 | Aux contact 52b (CB open)
BI6
BI7
BI8
5.2 Binary Outputs (BO)
Force each output contact via PCM600 Test menu (output control / forcing) or by asserting the function block that drives it. Verify continuity at the relay terminals AND at the destination.
BO Channel | Driven by / Function | Force method | Continuity (Y/N) | Operates target (Y/N) | Status | Notes | Initials
PO1 | Master Trip | PCM600 Force
PO2 | Reclose (if applicable) | PCM600 Force
SO1 | Alarm | PCM600 Force
SO2 |  | PCM600 Force
SO3 |  | PCM600 Force
SO4 |  | PCM600 Force
PCM600 Force
PCM600 Force
PCM600 Force
PCM600 Force

## 6. Element Tracker
Protection Element Tracker
Identify enabled functions, when each was last tested, and which to test this visit. Rotate elements between visits.
ANSI | ABB function block | Function description | Enabled? (Y/N) | Last tested (date) | Test this visit? (Y/N) | Result
49M | T1PTTR1 | Thermal overload — motor
50 | PHIPTOC1 | Instantaneous overcurrent (3-phase)
51 | PHLPTOC1 | Definite/inverse-time overcurrent (3-phase)
50N/51N | EFIPTOC1/EFHPTOC1 | Non-directional earth fault (Io)
46 | NSPTOC1 | Negative-sequence overcurrent / phase unbalance
48 | STTPMSU1 | Locked rotor / excessive start time
51LR | JAMPTOC1 | Locked rotor during operation (Jam)
66 | STTPMSU1 | Number of starts limiter
37 | PHPIOC1 | Loss of load / undercurrent
14 | ZSCPDIS1 | Zero speed / stall (when applicable)
38 | RTD | Bearing / stator winding temperature (via RTD module)
27 | PHPTUV1 | Undervoltage (if VT option fitted)
59 | PHPTOV1 | Overvoltage (if VT option fitted)

## 7. Element Results
Per-Element Test Results
Record one row per element tested this visit. Pickup and timing errors and pass/fail are calculated automatically.
# | ANSI | Function | Setting tested | Pickup setting | Pickup measured | Pickup err % | Time setting (s) | Time measured (s) | Time err % | Result | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16

## 8. Post-Test
Post-Test Checklist
8.1 Settings re-comparison (as-left vs. master)
# | Check | Status | Notes / Value | Initials
1 | Read parameter setting from IED via PCM600; save with prefix "asleft_<Asset>_<YYYYMMDD>.pcmi".
2 | Compared as-left vs. approved master parameter setting.
3 | Zero unauthorised differences remain.
4 | Any temporarily disabled function blocks have been re-enabled.
5 | Confirm thermal replica is at sensible value after restore (PCM600 measurement view).
6 | Re-enable any locked-rotor protection that was disabled for testing.
8.2 Clear events / reset records
# | Check | Status | Notes / Value | Initials
7 | Cleared event recorder.
8 | Cleared disturbance records (if appropriate / per Contact procedure).
9 | Reset LED indication on front panel.
10 | Cleared trip indications.
8.3 Time synchronisation
# | Check | Status | Notes / Value | Initials
11 | Re-read IED date/time.
12 | If drift outside tolerance, set IED time to reference.
13 | Time sync (IRIG-B / NTP / PTP) reports healthy.
14 | Final drift within tolerance.
8.4 Plant restoration
# | Check | Status | Notes / Value | Initials
15 | Disconnected all test leads from relay terminals.
16 | Replaced all test block links / reinstated VT MCBs.
17 | Removed CT shorting links; verified CT secondary continuity to source.
18 | Restored trip and lockout output links / re-enabled trips.
19 | Verified no targets / alarms / IRF active on IED.
20 | Confirm SCADA / DCS analogue values match IED metering live.
21 | Re-energised VTs; sensible secondary voltages on IED metering view.
22 | Operations / control room notified work complete.
23 | Permit returned and isolations removed (LOTO removed).
8.5 Final self-test
# | Check | Status | Notes / Value | Initials
24 | Self-supervision in PCM600 reports OK with no IRF or warnings.
25 | IED in service / ENABLED state per plant requirements.
26 | Final screenshots captured (Self-supervision / Measurements / IED status).

## 9. Files & Sign-Off
Findings Log & Sign-Off
Findings, Defects & Recommendations (detailed log)
# | Finding / Defect | Severity | Closed?
1
2
3
4
5
6
7
8
Sign-Off
Tester name
Tester signature
Date
Witness name
Witness signature
Date
Authorising engineer (acceptance)
Signature
Date
Overall test result (from Cover sheet) | 0