## 1. Cover
PROTECTION RELAY TEST RESULTS
SEL-300G Generator Protection Relay — Live Results Template
Test Summary & Findings (filled in at end of visit)
Overall outcome
Test completion date
Summary & Findings
Test Information
Site / Power station
Asset identifier (line / generator / unit)
Work order / Job number
Reason for test | Routine
Test date (start)
Test date (finish)
Personnel
Tester (name)
Tester signature
Witness / 2nd person
Witness signature
Authorising engineer
Relay Under Test
Relay model | SEL-300G
Relay tag / functional ID
Serial number
Firmware (FID) version
Part number
Panel / cubicle location
Active settings group
Breaker arrangement / unit type
Notes
CT / VT Ratios (primary : secondary) — drives Expected Primary in analogue tables
Ratio | Primary | Secondary | Ratio (P/S) | Unit (V/A)
Main VT (line-N) | 11000 | 63.5 |  | V or A
Neutral VT (3V0) | 11000 | 110 |  | V or A
Stator-side CT | 1000 | 5 |  | V or A
Neutral-side CT | 1000 | 5 |  | V or A
Test Tolerances (drives auto pass/fail)
Voltage magnitude tolerance (%) | 1
Current magnitude tolerance (%) | 1
Phase angle tolerance (°) | 1
Element pickup tolerance (%) | 5
Element timing tolerance (%) | 5
Auto-rolled-up status (calculated)
Analogue inputs
Element tests
Auto overall
Legend: blue text = user input. Grey/auto cells are calculated. Yellow tolerance cells drive PASS/FAIL.

## 2. Equip & Refs
Test Equipment, Drawings & Reference Documents
Test Equipment Used
Equipment | Make / Model | Serial No. | Last Cal. Date | Cal. Due | Cal. Cert. No.
Three-phase test set | Omicron CMC
Laptop / SEL AcSELerator |  | N/A | N/A | N/A | N/A
Multimeter
Reference Drawings
Drawing No. | Title | Revision | Date | Notes
Single line diagram
Schematic — protection AC
Schematic — protection DC / trip
Panel general arrangement
Test File & Reference Document Locations
Note: paste the SharePoint URL into each cell. Excel will turn it into a clickable link automatically.
Omicron test file (.occ filename)
SharePoint — Settings files (URL) | https://sharepoint.contactenergy.co.nz/
SharePoint — Omicron electronic test file (URL) | https://sharepoint.contactenergy.co.nz/
SharePoint — Protection Functional Report (URL) | https://sharepoint.contactenergy.co.nz/
SharePoint — Other (events, SOE, reports) (URL) | https://sharepoint.contactenergy.co.nz/

## 3. Pre-Test
Pre-Test Checklist
3.1 Visual Inspection
# | Check | Status | Notes / Value | Initials
1 | Relay mounted securely; no physical damage to fascia or terminals.
2 | All wiring terminations tight (sample); no signs of overheating.
3 | Front-panel LEDs illuminate during lamp test.
4 | No active alarms or target LEDs on arrival.
5 | Aux supply voltage at relay terminals within tolerance (record value in Notes).
3.2 Connect to Relay & Verify Status
# | Check | Status | Notes / Value | Initials
6 | Communications established with relay (front / rear port).
7 | STATUS / STA command — self-test OK, no failures.
8 | MET command — live values sane.
9 | FID and Part Number recorded in Cover sheet.
3.3 Time / Clock Check
# | Check | Status | Notes / Value | Initials
10 | Read relay date/time; record drift vs. reference (Notes).
11 | Identified source of time sync (IRIG-B, NTP, manual).
3.4 Event Records
# | Check | Status | Notes / Value | Initials
12 | Downloaded all events (HIS / EVE) and saved to job folder.
13 | Number of events on relay (record in Notes).
14 | Reviewed events for unexpected operations / pickups since last test.
15 | Cross-referenced anomalies with operations / SCADA / fault log.
3.5 Sequence of Events (SOE)
# | Check | Status | Notes / Value | Initials
16 | Downloaded SER / SOE buffer and saved to job folder.
17 | Reviewed for unexpected element pickups, drop-outs or input chatter.
3.6 Settings — As-Found
# | Check | Status | Notes / Value | Initials
18 | Read full settings; saved with prefix "asfound_<Asset>_<YYYYMMDD>".
19 | Compared as-found vs. master settings (AcSELerator compare).
20 | All differences documented (record file name in Notes).
21 | Differences are authorised changes only.
3.7 Settings vs. Protection Functional Description
# | Check | Status | Notes / Value | Initials
22 | Enabled functions match functional description.
23 | Key element settings match document.
24 | CT and VT ratios entered match nameplate / SLD and section on Cover.
25 | Trip matrix / output mapping matches functional description.

## 4. Analogue Inputs
Analogue Input Verification — PRIMARY values
Inject secondary; relay reports primary internally using configured ratios on Cover. Expected Primary, error % and pass/fail are calculated automatically. Magnitude tolerance: TolV_pct/TolI_pct, angle tolerance: TolAngle_deg.
If Expected Primary shows blank, check the corresponding CT/VT ratio is filled in on the Cover sheet.
4.1 VT Inputs — Three-Phase Voltage Injection (Primary verification)
Step | Injected (V sec) | Inj Angle (°) | Phase / Input | Expected Primary (V or kV) | Relay Primary | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 63.5 | 0 | L1 (VA)
1 | 63.5 | -120 | L2 (VB)
1 | 63.5 | 120 | L3 (VC)
2 | 110 | 0 | L1 (VA)
2 | 110 | -120 | L2 (VB)
2 | 110 | 120 | L3 (VC)
3 | 30 | 0 | L1 (VA)
3 | 30 | -120 | L2 (VB)
3 | 30 | 120 | L3 (VC)
4.2 Neutral Voltage Input — VN / 3V0 (Primary verification)
Step | Injected (V sec) | Inj Angle (°) | Phase / Input | Expected Primary (V or kV) | Relay Primary | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 10 | 0 | VN / 3V0
2 | 30 | 0 | VN / 3V0
3 | 60 | 0 | VN / 3V0
4 | 100 | 0 | VN / 3V0
4.3 Stator-Side CT — Three-Phase Current Injection (Primary verification)
Step | Injected (A sec) | Inj Angle (°) | Phase / Input | Expected Primary (A) | Relay Primary | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 1 | 0 | L1 stator
1 | 1 | -120 | L2 stator
1 | 1 | 120 | L3 stator
2 | 5 | 0 | L1 stator
2 | 5 | -120 | L2 stator
2 | 5 | 120 | L3 stator
3 | 0.2 | 0 | L1 stator
3 | 0.2 | -120 | L2 stator
3 | 0.2 | 120 | L3 stator
4.4 Neutral-Side CT — Three-Phase Current Injection (Primary verification)
Step | Injected (A sec) | Inj Angle (°) | Phase / Input | Expected Primary (A) | Relay Primary | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 1 | 0 | L1 neutral
1 | 1 | -120 | L2 neutral
1 | 1 | 120 | L3 neutral
2 | 5 | 0 | L1 neutral
2 | 5 | -120 | L2 neutral
2 | 5 | 120 | L3 neutral
3 | 0.2 | 0 | L1 neutral
3 | 0.2 | -120 | L2 neutral
3 | 0.2 | 120 | L3 neutral

## 5. Binary IO
Binary Input / Output Functional Tests
5.1 Relay Binary Inputs
Input | Description / Source | Pickup V (V) | Asserted? (Y/N) | SER captured? (Y/N) | Status | Notes | Initials
IN101
IN102
IN103
IN104
IN105
IN106
IN201
IN202
5.2 Relay Binary Outputs
Output | Driven by / Function | Pulse cmd. | Continuity (Y/N) | Operates target (Y/N) | Status | Notes | Initials
OUT101 |  | PUL OUT101
OUT102 |  | PUL OUT102
OUT103 |  | PUL OUT103
OUT104 |  | PUL OUT104
OUT105 |  | PUL OUT105
OUT201 |  | PUL OUT201
OUT202 |  | PUL OUT202
OUT203 |  | PUL OUT203

## 6. Element Tracker
Protection Element Tracker
ANSI | Function | Enabled? (Y/N) | Last tested (date) | Test this visit? (Y/N) | Result | Notes
87G | Generator differential
87T | Unit / step-up transformer differential
64S | 100% stator earth fault (3rd harm. / inj.)
59N | Stator earth fault (95%)
64F | Field (rotor) earth fault
40 | Loss of field / under-excitation
32 | Reverse / directional power
46 | Negative sequence overcurrent
24 | Volts/Hz (overexcitation)
27 | Undervoltage
59 | Overvoltage
81 O | Over-frequency
81 U | Under-frequency
81 R | Rate-of-change of frequency (df/dt)
21 | Distance (system back-up)
50/51 | Phase overcurrent / inverse-time
50N/51N | Neutral overcurrent
49 | Stator thermal
78 | Out-of-step / pole slip
60 | VT supervision / fuse failure
50BF | Breaker failure
25 | Synchronism / dead-bus check

## 7. Element Results
Per-Element Test Results
# | ANSI | Function | Setting tested | Pickup setting | Pickup measured | Pickup err % | Time setting (s) | Time measured (s) | Time err % | Result | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16

## 8. Post-Test
Post-Test Checklist
8.1 Settings re-comparison (as-left vs. master)
# | Check | Status | Notes / Value | Initials
1 | Read settings; saved with prefix "asleft_<Asset>_<YYYYMMDD>".
2 | Compared as-left vs. master settings (AcSELerator).
3 | Zero unauthorised differences remain.
4 | Any temporarily disabled elements have been restored.
8.2 Clear events / reset targets
# | Check | Status | Notes / Value | Initials
5 | Cleared event history (HIS C / EVE C).
6 | Cleared SOE buffer (SER C).
7 | Reset targets (TAR R) and front-panel LEDs.
8 | Verified buffers are empty after clearing.
8.3 Time synchronisation
# | Check | Status | Notes / Value | Initials
9 | Re-read relay date/time.
10 | If drift outside tolerance, set relay time to reference.
11 | IRIG-B / NTP / SNTP synchronisation healthy (status word).
12 | Final drift within tolerance.
8.4 Plant restoration
# | Check | Status | Notes / Value | Initials
13 | Disconnected all test leads from relay terminals.
14 | Replaced all test block links / reinstated VT MCBs.
15 | Removed CT shorting links; verified continuity to source.
16 | Restored trip and lockout output links / re-enabled trips.
17 | No targets / alarms remain active on relay or panel.
18 | SCADA / DCS analogue values match relay metering live.
19 | Re-energised VTs; sensible secondary voltages on relay.
20 | Operations / control room notified work complete.
21 | Permit returned and isolations removed (LOTO removed).
8.5 Final self-test
# | Check | Status | Notes / Value | Initials
22 | STATUS reports OK with no warnings or failures.
23 | Relay in service / ENABLED state per plant requirements.
24 | Final screenshots captured (STATUS / METER / TARGET).

## 9. Files & Sign-Off
Findings Log & Sign-Off
Findings, Defects & Recommendations (detailed log)
# | Finding / Defect | Severity | Closed?
1
2
3
4
5
6
7
8
Sign-Off
Tester name
Tester signature
Date
Witness name
Witness signature
Date
Authorising engineer (acceptance)
Signature
Date
Overall test result (from Cover sheet)