## 1. Cover
PROTECTION RELAY TEST RESULTS
ABB REF615 Feeder Protection Relay — Live Results Template
Test Summary & Findings (filled in at end of visit)
Overall outcome
Test completion date
Summary & Findings
Test Information
Site / Substation
Asset identifier (feeder / motor / transformer)
Work order / Job number
Reason for test | Routine
Test date (start)
Test date (finish)
Personnel
Tester (name)
Tester signature
Witness / 2nd person
Witness signature
Authorising engineer
Relay Under Test
Relay model | REF615
Relay function | Feeder Protection (Relion 615 series)
Relay tag / functional ID
Order code / part number
Serial number
Firmware version
Panel / cubicle location
IED name (in PCM600 project)
Active settings group
CT / VT Ratios (primary : secondary) — drives Expected Primary in analogue tables
Ratio | Primary | Secondary | Ratio (P/S) | Unit (V/A)
Phase CT (3-phase) | 600 | 1 | 600 | V or A
Earth-fault Io CT (core-balance / residual) | 600 | 1 | 600 | V or A
Main VT (line-N) | 11000 | 63.5 | 173.2283 | V or A
Residual voltage Uo / 3Vo VT | 11000 | 110 | 100 | V or A
Test Tolerances (drives auto pass/fail)
Voltage magnitude tolerance (%) | 1
Current magnitude tolerance (%) | 1
Phase angle tolerance (°) | 1
Element pickup tolerance (%) | 5
Element timing tolerance (%) | 5
Auto-rolled-up status (calculated)
Analogue inputs
Element tests
Auto overall | INCOMPLETE

## 2. Equip & Refs
Test Equipment, Drawings & Reference Documents
Test Equipment Used
Three-phase test set | Omicron CMC | Serial number | Cal Date
Laptop / PCM600 |  | N/A | N/A
Multimeter
PCM version
Dvice driver version
Reference Drawings
Drawing No. | Title | Revision | Date | Notes
Single line diagram
Schematic — protection AC
Schematic — protection DC / trip
Panel general arrangement
Application configuration drawing (PCM600)
Test File & Reference Document Locations
Note: paste the SharePoint URL into each cell. Excel will turn it into a clickable link automatically.
Omicron test file (.occ filename)
SharePoint — PCM600 project | https://sharepoint.contactenergy.co.nz/
SharePoint — Omicron electronic test file | https://sharepoint.contactenergy.co.nz/
SharePoint — Protection Functional Report | https://sharepoint.contactenergy.co.nz/
SharePoint — Other (events, disturbance records) | https://sharepoint.contactenergy.co.nz/

## 3. Pre-Test
Pre-Test Checklist
3.1 Visual Inspection
# | Check | Status | Notes / Value | Initials
1 | Relay mounted securely; no physical damage to fascia or terminals.
2 | All wiring terminations tight (sample); no signs of overheating.
3 | Front-panel LCD, LEDs and pushbuttons all functional.
4 | No active alarms, IRF indication or trip LEDs on arrival.
5 | Aux supply voltage at relay terminals within tolerance (record in Notes).
3.2 Connect to Relay & Verify Status (via PCM600)
# | Check | Status | Notes / Value | Initials
6 | Open PCM600; connect to IED via front Ethernet (IEC 61850 / FTP).
7 | IED status reads OK in PCM600 (no IRF, no failures).
8 | Measurements view in PCM600 shows sane analogue values for current operating state.
9 | IED type, order code and firmware version recorded on Cover sheet (match plant register).
10 | Self-supervision details captured (no warnings or service condition issues).
3.3 Time / Clock Check
# | Check | Status | Notes / Value | Initials
11 | Read IED date/time from PCM600 or HMI; record drift vs. reference (Notes).
12 | Time sync source identified (IRIG-B, SNTP/NTP, PTP, manual).
13 | Sync status reports healthy (where applicable).
3.4 Event Records
# | Check | Status | Notes / Value | Initials
14 | Read event records from IED via PCM600 (Disturbance Recorder).
15 | Disturbance records exported (COMTRADE) and saved to job folder.
16 | Reviewed event list for unexpected operations / pickups since last test.
17 | Cross-referenced anomalies with operations / SCADA / fault log.
3.5 Sequence of Events (Event recorder)
# | Check | Status | Notes / Value | Initials
18 | Event recorder list reviewed for unexpected element pickups or input bouncing.
19 | Communications-related events (channel loss, NTP loss, IRF) reviewed.
3.6 Settings — As-Found
# | Check | Status | Notes / Value | Initials
20 | Read parameter setting from IED via PCM600; save IED-specific .pcmi (or read whole project).
21 | Save with filename prefix "asfound_<Asset>_<YYYYMMDD>.pcmi".
22 | Compared as-found vs. approved master parameter setting.
23 | All differences documented (record compare report file name in Notes).
24 | Differences are authorised changes only.
3.7 Settings vs. Protection Functional Description
# | Check | Status | Notes / Value | Initials
25 | Enabled function blocks match functional description.
26 | Key element settings (pickup, time delay, characteristic) match document.
27 | CT and VT ratios in IED match nameplate / SLD and Cover sheet.
28 | Application configuration (trip matrix / logic) matches functional description.
29 | Binary input / output mapping matches functional description.

## 4. Analogue Inputs
Analogue Input Verification — PRIMARY values
Inject secondary; IED reports primary internally using configured ratios on Cover. Expected Primary, error % and pass/fail are calculated automatically. Magnitude tolerance: TolV_pct/TolI_pct, angle tolerance: TolAngle_deg.
If Expected Primary shows blank, check the corresponding CT/VT ratio is filled in on the Cover sheet.
4.1 Phase VT Inputs — Three-Phase Voltage Injection (Primary verification)
Step | Injected (V sec) | Inj Angle (°) | Phase / Input | Expected Primary (V or kV) | Relay Primary | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 63.5 | 0 | L1 (Ua) | 11000
1 | 63.5 | -120 | L2 (Ub) | 11000
1 | 63.5 | 120 | L3 (Uc) | 11000
2 | 110 | 0 | L1 (Ua) | 19055.1181
2 | 110 | -120 | L2 (Ub) | 19055.1181
2 | 110 | 120 | L3 (Uc) | 19055.1181
3 | 30 | 0 | L1 (Ua) | 5196.8504
3 | 30 | -120 | L2 (Ub) | 5196.8504
3 | 30 | 120 | L3 (Uc) | 5196.8504
4.2 Residual Voltage Input — Uo / 3Vo (Primary verification)
Step | Injected (V sec) | Inj Angle (°) | Phase / Input | Expected Primary (V or kV) | Relay Primary | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 10 | 0 | Uo | 1000
2 | 30 | 0 | Uo | 3000
3 | 60 | 0 | Uo | 6000
4 | 100 | 0 | Uo | 10000
4.3 Phase CT Inputs — Three-Phase Current Injection (Primary verification)
Step | Injected (A sec) | Inj Angle (°) | Phase / Input | Expected Primary (A) | Relay Primary | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 0.2 | 0 | L1 (IL1) | 120
1 | 0.2 | -120 | L2 (IL2) | 120
1 | 0.2 | 120 | L3 (IL3) | 120
2 | 1 | 0 | L1 (IL1) | 600
2 | 1 | -120 | L2 (IL2) | 600
2 | 1 | 120 | L3 (IL3) | 600
3 | 5 | 0 | L1 (IL1) | 3000
3 | 5 | -120 | L2 (IL2) | 3000
3 | 5 | 120 | L3 (IL3) | 3000
4.4 Earth-Fault Io Input — Single-Phase Current Injection (Primary verification)
Step | Injected (A sec) | Inj Angle (°) | Phase / Input | Expected Primary (A) | Relay Primary | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 0.05 | 0 | Io | 30
2 | 0.2 | 0 | Io | 120
3 | 1 | 0 | Io | 600

## 5. Binary IO
Binary Input / Output Functional Tests
5.1 Binary Inputs (BI)
Apply rated voltage to each binary input (or operate the source field device) and confirm the input asserts in PCM600 (Function blocks / Event recorder).
BI Channel | Description / Source | Pickup V (V) | Asserted? (Y/N) | Event captured? (Y/N) | Status | Notes | Initials
BI1 | Trip from external (e.g. BBP / 87)
BI2 | Local/Remote selector
BI3 | Reset external
BI4 | Aux contact 52a (CB closed)
BI5 | Aux contact 52b (CB open)
BI6 | Block 79 reclose
BI7
BI8
5.2 Binary Outputs (BO)
Force each output contact via PCM600 Test menu (output control / forcing) or by asserting the function block that drives it. Verify continuity at the relay terminals AND at the destination.
BO Channel | Driven by / Function | Force method | Continuity (Y/N) | Operates target (Y/N) | Status | Notes | Initials
PO1 | Master Trip (line CB) | PCM600 Force
PO2 | Reclose | PCM600 Force
SO1 | Alarm | PCM600 Force
SO2 | Block 79 to remote | PCM600 Force
SO3 |  | PCM600 Force
SO4 |  | PCM600 Force
PCM600 Force
PCM600 Force
PCM600 Force
PCM600 Force

## 6. Element Tracker
Protection Element Tracker
Identify enabled functions, when each was last tested, and which to test this visit. Rotate elements between visits.
For these relays it is fine to use the build in test function to prove the element operates and closes the corect outputs possibly even check that
That the outputs open the circuit breaker, if you can test a function with an omicron without alterning settings then do that element.
ANSI | ABB function block | Function description | Enabled? (Y/N) | Last tested (date) | Test this visit? (Y/N) | Result
50 | PHIPTOC1 | Instantaneous overcurrent (3-phase)
51 | PHLPTOC1 | Definite/inverse-time overcurrent (3-phase)
50N | EFIPTOC1 | Instantaneous earth-fault overcurrent (Io)
51N | EFHPTOC1 | Inverse-time earth-fault overcurrent (Io)
67 | DPHHPDOC1 | Directional phase overcurrent
67N | DEFLPDEF1 | Directional earth-fault overcurrent (admittance / Io·cosφ)
27 | PHPTUV1 | Undervoltage (3-phase)
59 | PHPTOV1 | Overvoltage (3-phase)
59N | ROVPTOV1 | Residual overvoltage (3Vo)
81 O | FRPFRQ1 | Over-frequency
81 U | FRPFRQ1 | Under-frequency
81 R | FRPFRQ1 | Rate-of-change of frequency (df/dt)
47 | PSPTUV1 | Negative-sequence / phase-reversal
60 | SEQRFUF1 | VT supervision / fuse failure
79 | DARREC1 | Auto-recloser
25 | SECRSYN1 | Synchronism / energy check (if fitted)
21FL | SCEFRFLO1 | Fault locator (if fitted)
46 | NSPTOC1 | Negative-sequence overcurrent

## 7. Element Results
Per-Element Test Results
Record one row per element tested this visit. Pickup and timing errors and pass/fail are calculated automatically.
# | ANSI | Function | Setting tested | Pickup setting | Pickup measured | Pickup err % | Time setting (s) | Time measured (s) | Time err % | Result | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Can refer to Omicron test file, try and test a single point shot with out changing any setting
For 615 Series of relays consider using the build in test functions to check the element operates and operates the out put or trips the circuit breaker

## 8. Post-Test
Post-Test Checklist
8.1 Settings re-comparison (as-left vs. master)
# | Check | Status | Notes / Value | Initials
1 | Read parameter setting from IED via PCM600; save with prefix "asleft_<Asset>_<YYYYMMDD>.pcmi".
2 | Compared as-left vs. approved master parameter setting.
3 | Zero unauthorised differences remain.
4 | Any temporarily disabled function blocks have been re-enabled.
5 | Re-enable auto-recloser if it was blocked.
6 | Confirm 79 lockout state is normal (not locked-out from test pulses).
8.2 Clear events / reset records
# | Check | Status | Notes / Value | Initials
7 | Cleared event recorder.
8 | Cleared disturbance records (if appropriate / per Contact procedure).
9 | Reset LED indication on front panel.
10 | Cleared trip indications.
8.3 Time synchronisation
# | Check | Status | Notes / Value | Initials
11 | Re-read IED date/time.
12 | If drift outside tolerance, set IED time to reference.
13 | Time sync (IRIG-B / NTP / PTP) reports healthy.
14 | Final drift within tolerance.
8.4 Plant restoration
# | Check | Status | Notes / Value | Initials
15 | Disconnected all test leads from relay terminals.
16 | Replaced all test block links / reinstated VT MCBs.
17 | Removed CT shorting links; verified CT secondary continuity to source.
18 | Restored trip and lockout output links / re-enabled trips.
19 | Verified no targets / alarms / IRF active on IED.
20 | Confirm SCADA / DCS analogue values match IED metering live.
21 | Re-energised VTs; sensible secondary voltages on IED metering view.
22 | Operations / control room notified work complete.
23 | Permit returned and isolations removed (LOTO removed).
8.5 Final self-test
# | Check | Status | Notes / Value | Initials
24 | Self-supervision in PCM600 reports OK with no IRF or warnings.
25 | IED in service / ENABLED state per plant requirements.
26 | Final screenshots captured (Self-supervision / Measurements / IED status).

## 9. Files & Sign-Off
Findings Log & Sign-Off
Findings, Defects & Recommendations (detailed log)
# | Finding / Defect | Severity | Closed?
1
2
3
4
5
6
7
8
Sign-Off
Tester name
Tester signature
Date
Witness name
Witness signature
Date
Authorising engineer (acceptance)
Signature
Date
Overall test result (from Cover sheet) | 0
Documentation Yes/No Notes
Omicron test file on SharePoint
As Left Settings on Sharepoint
Prot Database Updated
Job closed in SAP