## 1. Cover
PROTECTION RELAY TEST RESULTS
ABB REU615 Voltage Protection Relay — Live Results Template
Test Summary & Findings (filled in at end of visit)
Overall outcome
Test completion date
Summary & Findings
Test Information
Site / Substation
Asset identifier (feeder / motor / transformer)
Work order / Job number
Reason for test | Routine
Test date (start)
Test date (finish)
Personnel
Tester (name)
Tester signature
Witness / 2nd person
Relay Under Test
Relay model | REU615
Relay function | Voltage Protection (Relion 615 series)
Relay tag / functional ID
Order code / part number
Serial number
Firmware version
Panel / cubicle location
IED name (in PCM600 project)
Active settings group
CT / VT Ratios (primary : secondary) — drives Expected Primary in analogue tables
Ratio | Primary | Secondary | Ratio (P/S) | Unit (V/A)
Main VT (line-N) | 11000 | 63.5 | 173.2283 | V or A
Residual voltage Uo / 3Vo VT | 11000 | 110 | 100 | V or A
Test Tolerances (drives auto pass/fail)
Voltage magnitude tolerance (%) | 1
Current magnitude tolerance (%) | 1
Phase angle tolerance (°) | 1
Element pickup tolerance (%) | 5
Element timing tolerance (%) | 5
Auto-rolled-up status (calculated)
Analogue inputs
Element tests
Auto overall | INCOMPLETE

## 2. Equip & Refs
Test Equipment, Drawings & Reference Documents
Test Equipment Used
Three-phase test set | Omicron CMC | Serial | Cal date
Laptop / PCM600 |  | N/A | N/A
Multimeter
Reference Drawings
Drawing No. | Title | Revision | Date | Notes
Single line diagram
Schematic — protection AC
Schematic — protection DC / trip
Panel general arrangement
Application configuration drawing (PCM600)
Test File & Reference Document Locations
Note: paste the SharePoint URL into each cell. Excel will turn it into a clickable link automatically.
Omicron test file (.occ filename)
SharePoint — PCM600 project / settings files (URL) | https://sharepoint.contactenergy.co.nz/
SharePoint — Omicron electronic test file (URL) | https://sharepoint.contactenergy.co.nz/
SharePoint — Protection Functional Report (URL) | https://sharepoint.contactenergy.co.nz/
SharePoint — Other (events, disturbance records, COMTRADE) (URL) | https://sharepoint.contactenergy.co.nz/

## 3. Pre-Test
Pre-Test Checklist
3.1 Visual Inspection
# | Check | Status | Notes / Value | Initials
1 | Relay mounted securely; no physical damage to fascia or terminals.
2 | All wiring terminations tight (sample); no signs of overheating.
3 | Front-panel LCD, LEDs and pushbuttons all functional.
4 | No active alarms, IRF indication or trip LEDs on arrival.
5 | Aux supply voltage at relay terminals within tolerance (record in Notes).
3.2 Connect to Relay & Verify Status (via PCM600)
# | Check | Status | Notes / Value | Initials
6 | Open PCM600; connect to IED via front Ethernet (IEC 61850 / FTP).
7 | IED status reads OK in PCM600 (no IRF, no failures).
8 | Measurements view in PCM600 shows sane analogue values for current operating state.
9 | IED type, order code and firmware version recorded on Cover sheet (match plant register).
10 | Self-supervision details captured (no warnings or service condition issues).
3.3 Time / Clock Check
# | Check | Status | Notes / Value | Initials
11 | Read IED date/time from PCM600 or HMI; record drift vs. reference (Notes).
12 | Time sync source identified (IRIG-B, SNTP/NTP, PTP, manual).
13 | Sync status reports healthy (where applicable).
3.4 Event Records
# | Check | Status | Notes / Value | Initials
14 | Read event records from IED via PCM600 (Disturbance Recorder).
15 | Disturbance records exported (COMTRADE) and saved to job folder.
16 | Reviewed event list for unexpected operations / pickups since last test.
17 | Cross-referenced anomalies with operations / SCADA / fault log.
3.5 Sequence of Events (Event recorder)
# | Check | Status | Notes / Value | Initials
18 | Event recorder list reviewed for unexpected element pickups or input bouncing.
19 | Communications-related events (channel loss, NTP loss, IRF) reviewed.
3.6 Settings — As-Found
# | Check | Status | Notes / Value | Initials
20 | Read parameter setting from IED via PCM600; save IED-specific .pcmi (or read whole project).
21 | Save with filename prefix "asfound_<Asset>_<YYYYMMDD>.pcmi".
22 | Compared as-found vs. approved master parameter setting.
23 | All differences documented (record compare report file name in Notes).
24 | Differences are authorised changes only.
3.7 Settings vs. Protection Functional Description
# | Check | Status | Notes / Value | Initials
25 | Enabled function blocks match functional description.
26 | Key element settings (pickup, time delay, characteristic) match document.
27 | CT and VT ratios in IED match nameplate / SLD and Cover sheet.
28 | Application configuration (trip matrix / logic) matches functional description.
29 | Binary input / output mapping matches functional description.

## 4. Analogue Inputs
Analogue Input Verification — PRIMARY values
Inject secondary; IED reports primary internally using configured ratios on Cover. Expected Primary, error % and pass/fail are calculated automatically. Magnitude tolerance: TolV_pct/TolI_pct, angle tolerance: TolAngle_deg.
If Expected Primary shows blank, check the corresponding CT/VT ratio is filled in on the Cover sheet.
4.1 Phase VT Inputs — Three-Phase Voltage Injection (Primary verification)
Step | Injected (V sec) | Inj Angle (°) | Phase / Input | Expected Primary (V or kV) | Relay Primary | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 63.5 | 0 | L1 (Ua) | 11000
1 | 63.5 | -120 | L2 (Ub) | 11000
1 | 63.5 | 120 | L3 (Uc) | 11000
2 | 110 | 0 | L1 (Ua) | 19055.1181
2 | 110 | -120 | L2 (Ub) | 19055.1181
2 | 110 | 120 | L3 (Uc) | 19055.1181
3 | 30 | 0 | L1 (Ua) | 5196.8504
3 | 30 | -120 | L2 (Ub) | 5196.8504
3 | 30 | 120 | L3 (Uc) | 5196.8504
4.2 Residual Voltage Input — Uo / 3Vo (Primary verification)
Step | Injected (V sec) | Inj Angle (°) | Phase / Input | Expected Primary (V or kV) | Relay Primary | Relay Angle (°) | Mag Err (%) | Angle Err (°) | P / F | Notes
1 | 10 | 0 | Uo | 1000
2 | 30 | 0 | Uo | 3000
3 | 60 | 0 | Uo | 6000
4 | 100 | 0 | Uo | 10000

## 5. Binary IO
Binary Input / Output Functional Tests
5.1 Binary Inputs (BI)
Apply rated voltage to each binary input (or operate the source field device) and confirm the input asserts in PCM600 (Function blocks / Event recorder).
BI Channel | Description / Source | Pickup V (V) | Asserted? (Y/N) | Event captured? (Y/N) | Status | Notes | Initials
BI1 | Trip from external
BI2 | Local/Remote selector
BI3 | Reset external
BI4 | Block voltage protection
BI5
BI6
BI7
BI8
5.2 Binary Outputs (BO)
Force each output contact via PCM600 Test menu (output control / forcing) or by asserting the function block that drives it. Verify continuity at the relay terminals AND at the destination.
BO Channel | Driven by / Function | Force method | Continuity (Y/N) | Operates target (Y/N) | Status | Notes | Initials
PO1 | Trip (UFLS / UVLS contactor) | PCM600 Force
PO2 | Alarm | PCM600 Force
SO1 | Stage 2 trip | PCM600 Force
SO2 |  | PCM600 Force
SO3 |  | PCM600 Force
SO4 |  | PCM600 Force
PCM600 Force
PCM600 Force
PCM600 Force
PCM600 Force

## 6. Element Tracker
Protection Element Tracker
Identify enabled functions, when each was last tested, and which to test this visit. Rotate elements between visits.
For the 615 devices consider using the build in test functions to test tha the device operates correctly
If there is an element that is easy to do without having to alter settings then do that one.
ANSI | ABB function block | Function description | Enabled? (Y/N) | Last tested (date) | Test this visit? (Y/N) | Result
27 | PHPTUV1 | Undervoltage (3-phase)
59 | PHPTOV1 | Overvoltage (3-phase)
59N | ROVPTOV1 | Residual overvoltage (3Vo / Uo)
27R | PSPTUV1 | Reverse-phase / phase reversal (negative-seq voltage)
47 | PSPTUV1 | Phase-sequence voltage
27P | PSPTUV1 | Positive-sequence undervoltage
59P | PSPTOV1 | Positive-sequence overvoltage
81 O | FRPFRQ1 | Over-frequency
81 U | FRPFRQ1 | Under-frequency
81 R | FRPFRQ1 | Rate-of-change of frequency (df/dt)
24 | OEPVPH1 | Volts per Hertz (overexcitation)
60 | SEQRFUF1 | VT supervision / fuse failure
78 | OOSPVPH1 | Out-of-step / vector shift (if fitted)

## 7. Element Results
Per-Element Test Results
Record one row per element tested this visit. Pickup and timing errors and pass/fail are calculated automatically.
# | ANSI | Function | Setting tested | Pickup setting | Pickup measured | Pickup err % | Time setting (s) | Time measured (s) | Time err % | Result | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Refer to omicron file if you must, but try and create a few single point repetable tests that can be used for maintenance quick checks
Or use the values from an element that is easily testable
If settings have not changed and the device IO has been proved then is is not necessary spending too much time type testing.
Use a spare relay to type test protection relay or setting scheme

## 8. Post-Test
Post-Test Checklist
8.1 Settings re-comparison (as-left vs. master)
# | Check | Status | Notes / Value | Initials
1 | Read parameter setting from IED via PCM600; save with prefix "asleft_<Asset>_<YYYYMMDD>.pcmi".
2 | Compared as-left vs. approved master parameter setting.
3 | Zero unauthorised differences remain.
4 | Any temporarily disabled function blocks have been re-enabled.
5 | Re-enable load-shedding scheme outputs if they were blocked.
6 | Omicron Electronic test file
8.2 Clear events / reset records
# | Check | Status | Notes / Value | Initials
6 | Cleared event recorder.
7 | Cleared disturbance records (if appropriate / per Contact procedure).
8 | Reset LED indication on front panel.
9 | Cleared trip indications.
8.3 Time synchronisation
# | Check | Status | Notes / Value | Initials
10 | Re-read IED date/time.
11 | If drift outside tolerance, set IED time to reference.
12 | Time sync (IRIG-B / NTP / PTP) reports healthy.
13 | Final drift within tolerance.
8.4 Plant restoration
# | Check | Status | Notes / Value | Initials
14 | Disconnected all test leads from relay terminals.
15 | Replaced all test block links / reinstated VT MCBs.
16 | Removed CT shorting links; verified CT secondary continuity to source.
17 | Restored trip and lockout output links / re-enabled trips.
18 | Verified no targets / alarms / IRF active on IED.
19 | Confirm SCADA / DCS analogue values match IED metering live.
20 | Re-energised VTs; sensible secondary voltages on IED metering view.
21 | Operations / control room notified work complete.
22 | Permit returned and isolations removed (LOTO removed).
8.5 Final self-test
# | Check | Status | Notes / Value | Initials
23 | Self-supervision in PCM600 reports OK with no IRF or warnings.
24 | IED in service / ENABLED state per plant requirements.
25 | Final screenshots captured (Self-supervision / Measurements / IED status).

## 9. Files & Sign-Off
Findings Log & Sign-Off
Findings, Defects & Recommendations (detailed log)
# | Finding / Defect | Severity | Closed?
1
2
3
4
5
6
7
8
Sign-Off
Tester name
Tester signature
Date
Witness name
Witness signature
Date
Authorising engineer (acceptance)
Signature
Date
Overall test result (from Cover sheet) | 0
Documentation yes/No
Omicron test file on SharePoint
As Left Settings on Sharepoint
Prot Database Updated
Job closed in SAP