## 1. Cover
SEL-787 TRANSFORMER PROTECTION RELAY — TEST RESULTS TEMPLATE
1. RELAY IDENTIFICATION
Relay Type / Model | SEL-787
Relay ID (RID)
Terminal ID (TID)
Serial Number
Firmware ID (FID)
Checksum ID (CID)
Protected Equipment (transformer tag)
Site / Substation
Test Date
Test Engineer
2. TRANSFORMER AND CT/VT PARAMETERS
Parameter | Setting Label | Value | Units
Transformer MVA Rating | MVA |  | MVA
Winding 1 Nominal Voltage (L-L) | VWDG1 |  | kV
Winding 2 Nominal Voltage (L-L) | VWDG2 |  | kV
Winding 1 CT Connection | W1CT | WYE | WYE / DELTA
Winding 2 CT Connection | W2CT | WYE | WYE / DELTA
W1 CT Ratio — Primary | CTR1 (primary) |  | A primary
W1 CT Ratio — Secondary | CTR1 (secondary) | 5 | A secondary
W2 CT Ratio — Primary | CTR2 (primary) |  | A primary
W2 CT Ratio — Secondary | CTR2 (secondary) | 5 | A secondary
Neutral CT Ratio — Primary | CTRN (primary) |  | A primary
Neutral CT Ratio — Secondary | CTRN (secondary) | 5 | A secondary
VT Ratio — Primary | PTR (primary) |  | V primary
VT Ratio — Secondary | PTR (secondary) |  | V secondary
VT Connection Type | DELTA_Y | WYE | WYE / DELTA
Diff. TAP Winding 1 | TAP1 |  | A secondary
Diff. TAP Winding 2 | TAP2 |  | A secondary
W1 CT Connection Compensation | W1CTC |  | 0 = none
W2 CT Connection Compensation | W2CTC |  | 0 = none
3. TEST TOLERANCES (yellow cells are editable)
Voltage Magnitude Tolerance | 1 | %
Current Magnitude Tolerance | 1 | %
Angle Tolerance | 2 | degrees
Pickup Tolerance | 5 | %
Timing Tolerance | 5 | %
4. OVERALL TEST RESULT
Auto-calculated cross-check |  |  |  | (auto only — see signed result)
SIGNED OVERALL RESULT | PASS |  |  | PASS / PASS WITH NOTES / FAIL

## 2. Equip & Refs
EQUIPMENT & REFERENCES
TEST EQUIPMENT USED
Equipment | Manufacturer / Model | Asset / Serial No. | Cal. Due
DOCUMENTS & DRAWINGS
Document | Title / Description | Document No. | Rev
Relay Settings File (.sel / QuickSet)
AC Elementary / Schematic
DC Control Schematic
Relay Panel Wiring Diagram
Protection Coordination Study
Maintenance Work Order

## 3. Pre-Test
PRE-TEST CHECKS
3.1 COMMUNICATIONS & IDENTIFICATION
Check | Expected / Action | Result | Notes
Connect serial cable (SEL-C662) or Ethernet to relay | Terminal prompt '=' or '-' appears
Issue QUIT <Enter> — verify response header | RID and TID match asset register
Issue ACC <Enter> + Level 1 password | Access Level 1 granted
ENABLED LED illuminated (green, front panel) | LED ON = relay healthy and in service
Firmware ID (FID) — record string | Matches approved firmware version
Checksum ID (CID) — record string | Matches as-left checksum from last test
3.2 RELAY SELF-TEST STATUS (issue STA <Enter> at serial port)
All items should show OK. WARN items require STA C to clear; persistent FAIL items require relay replacement / SEL support. Record measured voltages for power supply rails.
Self-Test Item | Normal Range / Description | Status / Measured Value | Action if WARN or FAIL
FPGA | Mainboard FPGA — power-up and run-time CRC
GPSB | Back-plane (board-to-board) communications
HMI | Front-panel display / HMI interface
RAM | External and internal RAM read/write test
ROM / NON_VOL | Data flash checksum (non-volatile memory)
CR_RAM | Critical RAM — active settings checksum
CLOCK | Real-time clock chip communications
CID_FILE | CID (configured IED description) file access
CARD_C / CARD_D / CARD_E | Option card ID register checks
CT Board (CURRENT) | CT A/D board present; offset −50 to +50 mV
VT Board (CARD_E) | VT A/D board present; offset −50 to +50 mV (if fitted)
RTD module (if fitted) | Internal/external RTD comms OK
+0.9 V supply | 0.855 – 0.945 V
+1.2 V supply | 1.152 – 1.248 V
+1.5 V supply | 1.35 – 1.65 V
+1.8 V supply | 1.71 – 1.89 V
+2.5 V supply | 2.32 – 2.68 V
+3.3 V supply | 3.07 – 3.53 V
+3.75 V supply | 3.48 – 4.02 V
+5.0 V supply | 4.65 – 5.35 V
−1.25 V supply | −1.16 to −1.34 V
−5.0 V supply | −4.65 to −5.35 V
BATT (clock battery) | 2.3 – 3.5 V
HALARM relay word bit | Should be 0 (not asserted)
3.3 CLOCK / TIME SYNCHRONISATION
Check | Expected / Action | Result | Notes
Issue TIM <Enter> — relay time | Within 5 s of reference clock
Issue DAT <Enter> — relay date | Correct calendar date
Time source shown (Internal / IRIG-B) | IRIG-B if time-code input connected
Synchronise clock if out of tolerance | TIM hh:mm:ss DAT mm/dd/yy
3.4 EVENT RECORDS (pre-test baseline)
Check | Expected / Action | Result | Notes
Issue HIS <Enter> — review event history | No unexplained trips/alarms since last test
Issue SER <Enter> — review SER log | No unexpected HALARM / SALARM events
Issue SUM <Enter> — event summary | Review; record most recent event number
Issue EVE <Enter> — most recent event report | Review for unexpected operation
3.5 SETTINGS VERIFICATION
Check | Expected / Action | Result | Notes
Issue SHOW <Enter> — download all settings | Settings match approved file
CTR1 (W1 CT ratio) matches Cover sheet | As per relay data
CTR2 (W2 CT ratio) matches Cover sheet | As per relay data
CTRN (neutral CT ratio) matches Cover sheet | As per relay data
PTR (VT ratio) matches Cover sheet (if VT fitted) | As per relay data
MVA, VWDG1, VWDG2 match transformer nameplate | As per nameplate
W1CTC / W2CTC non-zero for grounded-WYE windings | See commissioning test worksheet
Active setting group correct | Group 1 or as applicable
Settings unchanged since last test | No unauthorised changes

## 4. Analogue Inputs
ANALOGUE INPUT VERIFICATION — PRIMARY VALUE CHECK
Verify the relay reports the correct PRIMARY value (Injected Secondary × CT or VT ratio). Use METER <Enter> or front-panel MAIN > Meters > Fundamental. Compare to Expected Primary calculated here from the ratios set on Cover sheet.
4.1 WINDING 1 PHASE CURRENTS (IAW1, IBW1, ICW1) [CTR1]
Ratio: Ratio_CTR1 defined on Cover sheet ¦ Tolerance: TolI_pct
Channel | Injected Sec. (A or V) | Inj. Angle (°) | Expected Primary (auto) | Relay Primary Reading | Relay Angle Reading | Mag Err % | Angle Err ° | Mag Tol % | Ang Tol ° | P/F
IAW1 — A-Phase Winding 1
IBW1 — B-Phase Winding 1
ICW1 — C-Phase Winding 1
4.2 WINDING 2 PHASE CURRENTS (IAW2, IBW2, ICW2) [CTR2]
Ratio: Ratio_CTR2 defined on Cover sheet ¦ Tolerance: TolI_pct
Channel | Injected Sec. (A or V) | Inj. Angle (°) | Expected Primary (auto) | Relay Primary Reading | Relay Angle Reading | Mag Err % | Angle Err ° | Mag Tol % | Ang Tol ° | P/F
IAW2 — A-Phase Winding 2
IBW2 — B-Phase Winding 2
ICW2 — C-Phase Winding 2
4.3 NEUTRAL CURRENT (IN) [CTRN] — if neutral CT fitted
Ratio: Ratio_CTRN defined on Cover sheet ¦ Tolerance: TolI_pct
Channel | Injected Sec. (A or V) | Inj. Angle (°) | Expected Primary (auto) | Relay Primary Reading | Relay Angle Reading | Mag Err % | Angle Err ° | Mag Tol % | Ang Tol ° | P/F
IN — Neutral current
4.4 VOLTAGE INPUTS (VA, VB, VC) [PTR] — if VT card fitted
Ratio: Ratio_PTR defined on Cover sheet ¦ Tolerance: TolV_pct
Channel | Injected Sec. (A or V) | Inj. Angle (°) | Expected Primary (auto) | Relay Primary Reading | Relay Angle Reading | Mag Err % | Angle Err ° | Mag Tol % | Ang Tol ° | P/F
VA — Phase A voltage
VB — Phase B voltage
VC — Phase C voltage
4.5 DIFFERENTIAL METER CHECK (METER DIF <Enter> or MAIN > Meters > Differential)
Under balanced load: IOP (operate) should be ≈ 0.00, IRT (restraint) ≈ load in TAP units. If MM = IOP/IRT > 0.10 investigate CT polarity, W1CTC/W2CTC compensation, and CT connections.
Diff Element | IOP (Operate, TAP) | IRT (Restraint, TAP) | MM = IOP/IRT | Accept if MM ≤ 0.10 | 2nd Harm (TAP) | 5th Harm (TAP) |  |  |  | Result
87-1 (DIFF1) |  |  |  | ≤ 0.10
87-2 (DIFF2) |  |  |  | ≤ 0.10
87-3 (DIFF3) if used |  |  |  | ≤ 0.10

## 5. Binary IO
BINARY I/O VERIFICATION
5.1 DIGITAL INPUTS — Pickup Verification
Apply rated control voltage to each input. Use front-panel MAIN > Targets > Row 21 or serial TARGET command to verify IN101/IN102 state changes 0→1.
Input No. | Function Label | Control Voltage Applied | Relay Word Bit | Result
IN101 | Digital Input 1 — edit to match schematics |  | IN101
IN102 | Digital Input 2 — edit to match schematics |  | IN102
IN301 | Optional DI — Input 1 (if card fitted) |  | IN301
IN302 | Optional DI — Input 2 (if card fitted) |  | IN302
IN303 | Optional DI — Input 3 (if card fitted) |  | IN303
IN304 | Optional DI — Input 4 (if card fitted) |  | IN304
5.2 DIGITAL OUTPUTS — Continuity Test
Force each output via serial (OUT101:=1 etc.) or CONTROL menu. Verify continuity through to trip coil / alarm annunciator. Restore all SELOGIC equations after test.
Output No. | Function Label | Force Command | Expected Result | P/F
OUT101 | TRIP / Main trip (edit label) | OUT101:=1 | Contact closes — continuity to trip coil
OUT102 | Alarm / Close (edit label) | OUT102:=1 | Contact closes — continuity verified
OUT103 | Auxiliary output (edit label) | OUT103:=1 | Contact closes — continuity verified
OUT301 | Optional DO — 1 (if card) | OUT301:=1 | Contact closes — continuity verified
OUT302 | Optional DO — 2 (if card) | OUT302:=1 | Contact closes — continuity verified

## 6. Element Tracker
PROTECTION ELEMENT TRACKER
# | Element ID | Description | Enabled (Y / N / NA) | Test Result Row | Result
1 | 87-1 | DIFF1 — Current Differential Element 1 (restrained + unrestrained)
2 | 87-2 | DIFF2 — Current Differential Element 2 (if fitted/enabled)
3 | 87-3 | DIFF3 — Current Differential Element 3 (if fitted/enabled)
4 | 50P1 | W1 Phase Instantaneous OC (50P11, 50P12, 50P13, 50P14)
5 | 50P2 | W2 Phase Instantaneous OC (50P21, 50P22, 50P23, 50P24)
6 | 50G1 | W1 Ground Instantaneous OC (50G11, 50G12)
7 | 50G2 | W2 Ground Instantaneous OC (50G21, 50G22)
8 | 50Q1 | W1 Neg-Seq Instantaneous OC (50Q11, 50Q12)
9 | 50Q2 | W2 Neg-Seq Instantaneous OC (50Q21, 50Q22)
10 | 51P1 | W1 Phase Time OC (51P1 — U1..U5, C1..C5 or user curve)
11 | 51P2 | W2 Phase Time OC (51P2)
12 | 51G1 | W1 Ground Time OC (51G1)
13 | 51G2 | W2 Ground Time OC (51G2)
14 | 51Q1 | W1 Neg-Seq Time OC (51Q1)
15 | 51Q2 | W2 Neg-Seq Time OC (51Q2)
16 | BF1 | Breaker Failure — Winding 1 (BFI1, BFT1)
17 | BF2 | Breaker Failure — Winding 2 (BFI2, BFT2)
18 | 50N1 | Neutral Instantaneous OC 1 (50N11, 50N12) — optional neutral CT
19 | 50N2 | Neutral Instantaneous OC 2 (50N21, 50N22) — optional
20 | 51N1 | Neutral Time OC (51N1) — optional
21 | REF | Restricted Earth Fault (REF1P, REF1F) — optional
22 | 27P1 | Undervoltage 1 (27P1, 27P1T) — requires VT card
23 | 27P2 | Undervoltage 2 (27P2, 27P2T) — requires VT card
24 | 59P1 | Overvoltage 1 (59P1, 59P1T) — requires VT card
25 | 59P2 | Overvoltage 2 (59P2, 59P2T) — requires VT card
26 | 59Q | Neg-Seq Overvoltage (59Q1, 59Q1T) — requires VT card
27 | 24D1 | Volts/Hertz Definite-Time (24D1, 24D1T) — requires VT card
28 | 24C2 | Volts/Hertz Inverse-Time (24C2, 24C2T) — requires VT card
29 | 32 | Directional Power (3PWR1, 3PWR2) — requires VT card
30 | 81D1 | Frequency — element 1 (81D1T) — requires VT card
31 | 81D2 | Frequency — element 2 (81D2T) — requires VT card
32 | 81D3 | Frequency — element 3 (81D3T) — requires VT card
33 | 81D4 | Frequency — element 4 (81D4T) — requires VT card
34 | RTD | RTD Thermal Protection (RTDT, RTDFLT) — requires RTD card

## 7. Element Results
PROTECTION ELEMENT TEST RESULTS
Setting column = relay pickup setting (secondary A, V, or %). Measured Pickup = value at which relay output asserted during injection. Pickup Err % = auto-calculated. Result = PASS if ¦Err¦ ≤ TolPickup_pct.
Element | Description | Pickup Setting (sec A, V, %) | Measured Pickup | Pickup Err % | Measured Time (s) | Result
87-1 R | Differential restrained pickup — 87AP × TAP1 (A secondary)
87-1 U | Differential unrestrained pickup — U87P × TAP1 (A secondary)
87-2 R | Differential restrained pickup — 87AP × TAP2 (if enabled)
50P11 | W1 Phase Inst OC — Stage 1 (A secondary)
50P12 | W1 Phase Inst OC — Stage 2 (A secondary)
50P21 | W2 Phase Inst OC — Stage 1 (A secondary)
50P22 | W2 Phase Inst OC — Stage 2 (A secondary)
50G11 | W1 Ground Inst OC — Stage 1 (A secondary)
50G21 | W2 Ground Inst OC — Stage 1 (A secondary)
50Q11 | W1 Neg-Seq Inst OC — Stage 1 (A secondary)
50Q21 | W2 Neg-Seq Inst OC — Stage 1 (A secondary)
51P1 | W1 Phase TOC — pickup (A secondary)
51G1 | W1 Ground TOC — pickup (A secondary)
51Q1 | W1 Neg-Seq TOC — pickup (A secondary)
51P2 | W2 Phase TOC — pickup (A secondary)
51G2 | W2 Ground TOC — pickup (A secondary)
51Q2 | W2 Neg-Seq TOC — pickup (A secondary)
50N11 | Neutral Inst OC 1 (A secondary, if enabled)
51N1 | Neutral TOC — pickup (A secondary, if enabled)
REF1 | Restricted Earth Fault (A secondary, if enabled)
27P1 | Undervoltage 1 (V secondary, if enabled)
27P2 | Undervoltage 2 (V secondary, if enabled)
59P1 | Overvoltage 1 (V secondary, if enabled)
59P2 | Overvoltage 2 (V secondary, if enabled)
24D1 | Volts/Hertz definite-time (%, if enabled)
24C2 | Volts/Hertz inverse-time (%, if enabled)
32-1 | Directional Power 1 (kVA secondary, if enabled)
81D1 | Frequency 1 (Hz, if enabled)
81D2 | Frequency 2 (Hz, if enabled)
RTD | RTD trip threshold (°C, if fitted)
BFD1 | Breaker Failure 1 — BFD1 timer (s)
BFD2 | Breaker Failure 2 — BFD2 timer (s)

## 8. Post-Test
POST-TEST CHECKS
8.1 SETTINGS RESTORE & VERIFICATION
Check | Expected / Action | Result | Notes
Issue SHOW <Enter> — verify settings unchanged | Match approved settings file
All test-forced SELOGIC equations restored | OUT101:=, SV variables correct
Active setting group restored to normal | Group 1 or as applicable
ENABLED LED illuminated (green) | Relay in service
8.2 FINAL SELF-TEST (STA Command)
Check | Expected / Action | Result | Notes
Issue STA <Enter> — all items OK | No WARN or FAIL items
HALARM = 0 (no hardware alarm) | Relay word bit confirmed 0
SALARM = 0 (no software alarm) | Normal operating condition
Relay Enabled confirmed | 'Relay Enabled' shown in STA output
8.3 CLEAR TEST DATA BUFFERS
Issue the commands below at Access Level 1 or higher to clear data generated during testing, preventing contamination of operational records.
Serial Command | Action Performed | Completed | Notes
SUM R <Enter> | Reset event report and summary command buffers
SER R <Enter> | Reset Sequential Events Record buffer
LDP C <Enter> | Clear Load Profile Data
HIS C <Enter> | Clear event history (if required by procedure)
8.4 PLANT RESTORATION
Check | Expected / Action | Result | Notes
Remove test connections from CT / VT terminals | Field CTs and VTs reconnected
Restore control voltage wiring | All control circuits normal
Remove CT secondary shorting links | CT circuits not open-circuited
Verify relay measuring load current — METER command | Compare to substation panel meters
METER DIF check — IOP/IRT ≤ 0.10 under load | Differential balance confirmed on load
Cancel all outstanding LOTO permits | All permits cleared
Notify operations — relay returned to service | Operations informed and recorded

## 9. Files & Sign-Off
FILES INDEX & SIGN-OFF
OVERALL TEST RESULT (from Cover sheet)
Signed Overall Result
TEST ARTEFACTS INDEX
Artefact | File Name / SharePoint Location | Date Saved | Notes
Relay settings file (.sel / QuickSet project)
Pre-test event records (HIS, SER, EVE, SUM)
Post-test event records
Completed results template (this file)
Oscillography / disturbance records
Test photographs / site notes
DEFECTS / FINDINGS LOG
# | Defect Description | Action Taken / Work Order | Closed
1
2
3
4
5
6
SIGN-OFF
Role | Name (print) | Signature | Date
Test Engineer
Witness (Operations)
Approving Engineer