## 1. Cover
ABB RET670 TRANSFORMER PROTECTION IED — TEST RESULTS TEMPLATE
1. IED IDENTIFICATION
Relay Type / Model | RET670 v2.2 ANSI
IED Name (Station / Bay)
Description (Protected Equipment)
Serial Number
Ordering Number
Firmware Version
Production Date
PCM600 Project File Name (.pcm)
Site / Substation
Test Date / Test Engineer
2. TRANSFORMER AND CT/VT PARAMETERS (from PCM600 / TRM settings)
Parameter | PCM600 Setting | Value | Units
Transformer MVA Rating | Sr / MVA |  | MVA
Winding 1 (HV) Nominal Voltage | GBASVAL Ur W1 |  | kV primary (L-L)
Winding 2 (LV) Nominal Voltage | GBASVAL Ur W2 |  | kV primary (L-L)
Winding 3 (TV) Nominal Voltage | GBASVAL Ur W3 | N/A | kV (or N/A if 2-wdg)
Winding 1 CT Primary | CTprim1 |  | A primary
Winding 1 CT Secondary | CTsec1 | 1 | A secondary
Winding 2 CT Primary | CTprim2 |  | A primary
Winding 2 CT Secondary | CTsec2 | 1 | A secondary
Winding 3 CT Primary | CTprim3 | N/A | A primary (N/A if 2-wdg)
Winding 3 CT Secondary | CTsec3 | N/A | A secondary
VT Primary Voltage | VTprim (kV) |  | kV primary (L-L)
VT Secondary Voltage | VTsec (V) |  | V secondary (L-L)
W1 CT Connection Direction | CT_WyePoint1 | ToObject | ToObject / FromObject
Active Setting Group | ACTVGRP | 1 | 1–6
3. TEST TOLERANCES (yellow cells are editable)
Voltage Magnitude Tolerance | 1 | %
Current Magnitude Tolerance | 1 | %
Angle Tolerance | 2 | degrees
Pickup Tolerance | 5 | %
Timing Tolerance | 5 | %
4. OVERALL TEST RESULT
Auto-calculated cross-check | INCOMPLETE |  |  | (auto only — see signed result)
SIGNED OVERALL RESULT | PASS |  |  | PASS / PASS WITH NOTES / FAIL

## 2. Equip & Refs
EQUIPMENT & REFERENCES
TEST EQUIPMENT USED
Equipment | Manufacturer / Model | Asset / Serial No. | Cal. Due
DOCUMENTS & DRAWINGS
Document | Title / Description | Document No. | Rev
PCM600 Project File / Signal Matrix Tool (SMT)
AC Elementary / Schematic
DC Control Schematic
Transformer Protection Single-Line Diagram
Protection Coordination Study
Maintenance Work Order

## 3. Pre-Test
PRE-TEST CHECKS
3.1 COMMUNICATIONS & IDENTIFICATION
Check | Expected / Action | Result | Notes
Connect to IED via PCM600 or web browser (Ethernet) | PCM600 connects and IED tree populates
Confirm IED name matches asset register | LHMI: Main menu → Settings → IED name (TERMINALID)
Confirm firmware version | LHMI: Main menu → Diagnostics → IED status → Version
Confirm serial number | LHMI: Main menu → Diagnostics → IED status → Product info
Normal LED (green, fixed) illuminated | Green LED ON = IED healthy and in service
No active alarms on LHMI alarm LEDs | All alarm LEDs off (or known / accepted conditions only)
Active setting group confirmed | LHMI: Main menu → Settings → Setting group (ACTVGRP)
3.2 IED SELF-SUPERVISION (INTERRSIG — LHMI: Main menu → Diagnostics → IED status → Signals)
The INTERRSIG function block provides continuous hardware and software self-monitoring. All signals should be NORMAL (0). Any FAIL signal will assert the INTERNAL FAIL contact on the PSM module. Navigate LHMI: Main menu → Diagnostics → IED status → Internal events to review the event log (last 40 events, FIFO).
INTERRSIG Signal | Description / What it monitors | State (NORMAL / FAIL / WARN) | Action if not NORMAL
FAIL | General IED failure — INTERNAL FAIL contact asserted on PSM
WARNING | Warning condition — degraded operation, not yet a failure
RTCERROR | Real-time clock error — timekeeping or battery issue
TIMESYNCHERROR | Time synchronisation error — IRIG-B / IEEE 1588 / NTP loss
RTEERROR | Real-time execution error — protection task overrun
IEC61850ERROR | IEC 61850 communication error — GOOSE or MMS failure
WATCHDOG | Watchdog timer failure — CPU or task hang
LMDERROR | LDCM (Line Data Communication Module) error — if fitted
APPERROR | Application configuration error — PCM600 config mismatch
3.2 (cont.) HARDWARE MODULE STATUS (LHMI: Main menu → Diagnostics → Hardware)
Module | Description | Status (OK / FAIL) | Notes
PSM | DC supply health and INTERNAL FAIL relay contact
ADOne | A/D converter TRM — CT/VT channel offsets
ADTwo | Second A/D converter (if TRM has 2 A/D boards — e.g. TRM_12I)
BIM | Binary Input Module — all BIM cards fitted
BOM | Binary Output Module — all BOM cards fitted
IOM | Input/Output Module — combined BIM/BOM cards
MIM | mA Input Module — if fitted for analogue supervision
LDCM | Line Data Communication Module — if fitted
3.3 TIME SYNCHRONISATION
Check | Expected / Action | Result | Notes
LHMI: Main menu → Diagnostics → IED status → Time | IED time within 1 s of reference clock
Time source active (IRIG-B / IEEE 1588 / NTP / manual) | TIMESYNCHERROR = NORMAL; source shown as active
Confirm date and time correct | Check against substation master clock or GPS reference
3.4 EVENT RECORDS (pre-test baseline)
Check | Expected / Action | Result | Notes
LHMI: Main menu → Events — review disturbance records | No unexplained trips or alarms since last test
Note most recent event number | Baseline for post-test comparison
Review internal event list (INTERRSIG) | No historic FAIL or WARNING events outstanding
Confirm disturbance recorder cleared / downloaded | Oscillography available for any recent events
3.5 SETTINGS VERIFICATION (PCM600 → Upload from IED)
Check | Expected / Action | Result | Notes
Upload settings via PCM600 — compare to approved file | Settings match last approved PCM600 project
CTprim/CTsec W1 correct | As per Cover sheet
CTprim/CTsec W2 correct | As per Cover sheet
CTprim/CTsec W3 correct (if 3-winding) | N/A or as per Cover sheet
VTprim/VTsec correct (if VT fitted) | As per Cover sheet
T2WPDIF / T3WPDIF differential settings correct | Match approved coordination study
REFPDIF (87N) settings correct (if enabled) | Match approved settings
GBASVAL (Ur, Ir, Sr) correct | Match transformer nameplate
Active setting group as expected (ACTVGRP) | Group 1 or as applicable
No unauthorised changes since last test | Settings unchanged

## 4. Analogue Inputs
ANALOGUE INPUT VERIFICATION — PRIMARY VALUE CHECK
Verify the IED reports the correct PRIMARY value (Injected Secondary × CT or VT ratio). Use LHMI: Main menu → Measurements → [function block] to read primary values. All IED readings are in primary units (CTprim × secondary, VTprim × secondary).
4.1 WINDING 1 PHASE CURRENTS (IA-W1, IB-W1, IC-W1) [Ratio_CT_W1]
Ratio: Ratio_CT_W1 ¦ Tolerance: TolI_pct (defined names on Cover sheet)
Channel | Injected Sec. (A or V) | Inj. Angle (°) | Expected Primary (auto) | IED Primary Reading | IED Angle Reading | Mag Err % | Angle Err ° | Mag Tol % | Ang Tol ° | P/F
IA-W1 — Winding 1 Phase A | [7 empty] | 1 | 2 | —
IB-W1 — Winding 1 Phase B | [7 empty] | 1 | 2 | —
IC-W1 — Winding 1 Phase C | [7 empty] | 1 | 2 | —
4.2 WINDING 2 PHASE CURRENTS (IA-W2, IB-W2, IC-W2) [Ratio_CT_W2]
Ratio: Ratio_CT_W2 ¦ Tolerance: TolI_pct (defined names on Cover sheet)
Channel | Injected Sec. (A or V) | Inj. Angle (°) | Expected Primary (auto) | IED Primary Reading | IED Angle Reading | Mag Err % | Angle Err ° | Mag Tol % | Ang Tol ° | P/F
IA-W2 — Winding 2 Phase A | [7 empty] | 1 | 2 | —
IB-W2 — Winding 2 Phase B | [7 empty] | 1 | 2 | —
IC-W2 — Winding 2 Phase C | [7 empty] | 1 | 2 | —
4.3 WINDING 3 PHASE CURRENTS (IA-W3, IB-W3, IC-W3) [Ratio_CT_W3] — if 3-winding
Ratio: Ratio_CT_W3 ¦ Tolerance: TolI_pct (defined names on Cover sheet)
Channel | Injected Sec. (A or V) | Inj. Angle (°) | Expected Primary (auto) | IED Primary Reading | IED Angle Reading | Mag Err % | Angle Err ° | Mag Tol % | Ang Tol ° | P/F
IA-W3 — Winding 3 Phase A | [7 empty] | 1 | 2 | —
IB-W3 — Winding 3 Phase B | [7 empty] | 1 | 2 | —
IC-W3 — Winding 3 Phase C | [7 empty] | 1 | 2 | —
4.4 VOLTAGE INPUTS (VA, VB, VC) [Ratio_VT] — if VT fitted
Ratio: Ratio_VT ¦ Tolerance: TolV_pct (defined names on Cover sheet)
Channel | Injected Sec. (A or V) | Inj. Angle (°) | Expected Primary (auto) | IED Primary Reading | IED Angle Reading | Mag Err % | Angle Err ° | Mag Tol % | Ang Tol ° | P/F
VA — Phase A voltage | [7 empty] | 1 | 2 | —
VB — Phase B voltage | [7 empty] | 1 | 2 | —
VC — Phase C voltage | [7 empty] | 1 | 2 | —
4.5 DIFFERENTIAL BALANCE CHECK (LHMI: Main menu → Measurements → T2WPDIF / T3WPDIF → IOP, IRT)
Under balanced load: IOP (operate current) should be ≈ 0.0 pu, IRT (bias / restraint) ≈ load current in pu. If IOP/IRT > 0.05 pu, investigate CT polarity, CT_WyePoint direction settings, and CT connections. Currents are displayed in pu of GBASVAL Ir. Accept threshold: IOP ≤ 0.05 pu.
Diff Function | IOP (pu of Ir) | IRT (pu of Ir) | IOP/IRT | Accept if IOP ≤ 0.05 pu | 2nd Harm (pu) | 5th Harm (pu) |  |  |  | Result
T2WPDIF (87T) — 2-winding differential |  |  |  | IOP ≤ 0.05 pu | [5 empty] | —
T3WPDIF (87T) — 3-winding differential (if fitted) |  |  |  | IOP ≤ 0.05 pu | [5 empty] | —
HZPDIF (87) — High impedance diff (if fitted) |  |  |  | IOP ≤ 0.05 pu | [5 empty] | —

## 5. Binary IO
BINARY I/O VERIFICATION
5.1 BINARY INPUTS — Pickup Verification
Apply rated control voltage to each binary input. Navigate LHMI: Main menu → Test → Binary inputs — verify status changes 0→1. Alternatively view in PCM600 Signal Monitor.
Input No. | Function Label (edit from schematics) | Voltage Applied | LHMI / PCM600 Verification | Result
BI01 | Binary Input 1 — edit label |  | LHMI: Test → Binary inputs
BI02 | Binary Input 2 — edit label |  | LHMI: Test → Binary inputs
BI03 | Binary Input 3 — edit label |  | LHMI: Test → Binary inputs
BI04 | Binary Input 4 — edit label |  | LHMI: Test → Binary inputs
BI05 | Binary Input 5 — edit label |  | LHMI: Test → Binary inputs
BI06 | Binary Input 6 — edit label |  | LHMI: Test → Binary inputs
BI07 | Binary Input 7 — edit label |  | LHMI: Test → Binary inputs
BI08 | Binary Input 8 — edit label |  | LHMI: Test → Binary inputs
5.2 BINARY OUTPUTS — Continuity Test
Use LHMI: Main menu → Test → Binary outputs to force each output. Verify contact continuity through wiring to trip coil / alarm circuit. Restore all outputs to normal after test — exit Test mode.
Output No. | Function Label | LHMI Force Method | Expected Result | P/F
BO01 | Binary Output 1 — edit label | LHMI: Test → Binary outputs | Contact closes — verify continuity
BO02 | Binary Output 2 — edit label | LHMI: Test → Binary outputs | Contact closes — verify continuity
BO03 | Binary Output 3 — edit label | LHMI: Test → Binary outputs | Contact closes — verify continuity
BO04 | Binary Output 4 — edit label | LHMI: Test → Binary outputs | Contact closes — verify continuity
BO05 | Binary Output 5 — edit label | LHMI: Test → Binary outputs | Contact closes — verify continuity
BO06 | Binary Output 6 — edit label | LHMI: Test → Binary outputs | Contact closes — verify continuity
BO07 | Binary Output 7 — edit label | LHMI: Test → Binary outputs | Contact closes — verify continuity
BO08 | Binary Output 8 — edit label | LHMI: Test → Binary outputs | Contact closes — verify continuity

## 6. Element Tracker
PROTECTION ELEMENT TRACKER
Just test elements that don't need settings changes, use built in trip checks - use spare for type testing relay and setting scheme.
# | IEC 61850 / ANSI | Description | Enabled (Y / N / NA) | Plant Test | Result
1 | T2WPDIF (87T) | 2-Winding transformer differential — restrained (IminOp, SlopeA/B)
2 | T2WPDIF-U (87T) | 2-Winding transformer differential — unrestrained (IdMinUnre)
3 | T3WPDIF (87T) | 3-Winding transformer differential — restrained (if fitted)
4 | HZPDIF (87) | High impedance differential protection, single phase (if fitted)
5 | REFPDIF (87N) | Restricted earth fault — low impedance differential (if fitted)
6 | PSTPDIF (87T) | Self-adaptive 2-winding transformer differential (if fitted)
7 | OEXPVPH (24) | Overexcitation / Volts-per-Hertz protection (if VT fitted)
8 | CCSSPVC (87CCS) | Current circuit supervision (CCS) — open CT detection
9 | PHPIOC (50) | Instantaneous phase overcurrent — W1 or W2 side
10 | OC4PTOC-W1 (51/67) | Directional phase TOC, 4 steps — Winding 1 side
11 | OC4PTOC-W2 (51/67) | Directional phase TOC, 4 steps — Winding 2 side
12 | EFPIOC (50N) | Instantaneous residual overcurrent
13 | EF4PTOC-W1 (51N/67N) | Directional residual TOC, 4 steps — Winding 1
14 | EF4PTOC-W2 (51N/67N) | Directional residual TOC, 4 steps — Winding 2
15 | NS4PTOC (46I2) | Negative-phase-sequence overcurrent, 4 steps
16 | SDEPSDE (67N) | Sensitive directional residual OC and power protection (if fitted)
17 | VRPVOC (51V) | Voltage-restrained time overcurrent (if VT fitted)
18 | TRPTTR (49) | Thermal overload protection — 2 time constants
19 | LCPTTR / LFPTTR (26) | Thermal overload protection — 1 time constant
20 | CCRBRF-W1 (50BF) | Breaker failure protection — Winding 1 breaker
21 | CCRBRF-W2 (50BF) | Breaker failure protection — Winding 2 breaker
22 | STBPTOC (50STB) | Stub protection — disconnector open condition (if fitted)
23 | UV2PTUV (27) | Two-step undervoltage protection (if VT fitted)
24 | OV2PTOV (59) | Two-step overvoltage protection (if VT fitted)
25 | ROV2PTOV (59N) | Two-step residual overvoltage (if VT fitted)
26 | VDCPTDV (87V) | Voltage differential protection (if dual VT fitted)
27 | LOVPTUV (27) | Loss of voltage check (if VT fitted)
28 | GOPPDOP (32) | Directional overpower protection (if VT fitted)
29 | GUPPDUP (37) | Directional underpower protection (if VT fitted)
30 | SAPTUF (81) | Underfrequency protection — up to 10 stages (if VT fitted)
31 | SAPTOF (81) | Overfrequency protection — up to 6 stages (if VT fitted)
32 | SAPFRC (81R) | Rate-of-change of frequency (ROCOF, if VT fitted)
33 | SESRSYN (25) | Synchrocheck and energisation check (if fitted)
34 | TR1ATCC (90) | Automatic voltage control — tap changer, single (if fitted)
35 | SSIMG (63) | Insulation supervision — gas medium (SF6 pressure, if fitted)
36 | SSIML (71) | Insulation supervision — liquid (oil level / Buchholz, if fitted)
37 | LOLSPTR (26/49HS) | Transformer insulation loss of life monitoring (if fitted)
38 | FUFSPVC | Fuse failure supervision — voltage based (if VT fitted)
39 | CCPDSC (52PD) | Pole discordance protection (if fitted)

## 7. Element Results
PROTECTION ELEMENT TEST RESULTS
Setting column = relay pickup setting (secondary A, V, or pu). Measured Pickup = value at which IED output asserted during injection. Pickup Err % = auto-calculated. Result = PASS if ¦Err¦ ≤ TolPickup_pct.
It is not necessary to do all the elements, bench test on spare relay if you requre a complete test, test elements that don't require setting changes.
Element | Description | Pickup Setting (sec A, V, or pu) | Measured Pickup | Pickup Err % | Measured Time (s) | Result
T2WPDIF-R | 87T restrained differential pickup — IminOp (pu of Ir) |  |  |  |  | —
T2WPDIF-U | 87T unrestrained differential pickup — IdMinUnre (pu of Ir) |  |  |  |  | —
T3WPDIF-R | 87T 3-winding restrained pickup (if fitted, pu of Ir) |  |  |  |  | —
REFPDIF | 87N restricted earth fault pickup (A secondary, if enabled) |  |  |  |  | —
OEXPVPH | 24 overexcitation pickup — V/Hz (% of rated, if VT fitted) |  |  |  |  | —
PHPIOC | 50 phase instantaneous OC — pickup (A secondary) |  |  |  |  | —
OC4PTOC-W1-1 | 51/67 phase TOC W1 — stage 1 pickup (A secondary) |  |  |  |  | —
OC4PTOC-W1-2 | 51/67 phase TOC W1 — stage 2 pickup (A secondary) |  |  |  |  | —
OC4PTOC-W2-1 | 51/67 phase TOC W2 — stage 1 pickup (A secondary) |  |  |  |  | —
EFPIOC | 50N residual instantaneous OC — pickup (A secondary) |  |  |  |  | —
EF4PTOC-W1-1 | 51N/67N residual TOC W1 — stage 1 pickup (A secondary) |  |  |  |  | —
EF4PTOC-W2-1 | 51N/67N residual TOC W2 — stage 1 pickup (A secondary) |  |  |  |  | —
NS4PTOC-1 | 46I2 neg-seq OC — stage 1 pickup (A secondary) |  |  |  |  | —
SDEPSDE | 67N sensitive directional residual pickup (A secondary) |  |  |  |  | —
VRPVOC | 51V voltage-restrained OC pickup (A secondary, if VT fitted) |  |  |  |  | —
TRPTTR | 49 thermal overload — thermal trip level (A secondary) |  |  |  |  | —
LCPTTR | 26 thermal overload — 1 TC — trip level (A secondary) |  |  |  |  | —
CCRBRF-W1 | 50BF breaker failure W1 — current pickup + BFD timer (s) |  |  |  |  | —
CCRBRF-W2 | 50BF breaker failure W2 — current pickup + BFD timer (s) |  |  |  |  | —
UV2PTUV-1 | 27 undervoltage — stage 1 pickup (V secondary, if VT fitted) |  |  |  |  | —
UV2PTUV-2 | 27 undervoltage — stage 2 pickup (V secondary, if VT fitted) |  |  |  |  | —
OV2PTOV-1 | 59 overvoltage — stage 1 pickup (V secondary, if VT fitted) |  |  |  |  | —
ROV2PTOV-1 | 59N residual OV — stage 1 pickup (V secondary, if VT fitted) |  |  |  |  | —
GOPPDOP | 32 directional overpower pickup (W primary, if VT fitted) |  |  |  |  | —
SAPTUF-1 | 81 underfrequency — stage 1 pickup (Hz, if VT fitted) |  |  |  |  | —
SAPTOF-1 | 81 overfrequency — stage 1 pickup (Hz, if VT fitted) |  |  |  |  | —
SAPFRC-1 | 81R ROCOF — stage 1 pickup (Hz/s, if VT fitted) |  |  |  |  | —
SESRSYN | 25 synchrocheck — closing window (degrees, if fitted) |  |  |  |  | —
CCSSPVC | 87CCS current circuit supervision — alarm threshold (A secondary) |  |  |  |  | —

## 8. Post-Test
POST-TEST CHECKS
8.1 SETTINGS RESTORE & VERIFICATION
Check | Expected / Action | Result | Notes
Re-upload settings via PCM600 — verify unchanged | Match approved project file
Exit Test mode on LHMI | LHMI: Main menu → Test → Exit test mode
All forced binary outputs restored to normal | BOM cards de-energised
Active setting group restored to normal | Group 1 or as applicable
Normal LED (green, fixed) illuminated | IED in service
8.2 FINAL SELF-SUPERVISION CHECK (LHMI: Main menu → Diagnostics → IED status → Signals → INTERRSIG)
Signal | Expected | Status | Notes
FAIL | NORMAL (0)
WARNING | NORMAL (0)
RTCERROR | NORMAL (0)
TIMESYNCHERROR | NORMAL (0)
RTEERROR | NORMAL (0)
IEC61850ERROR | NORMAL (0)
WATCHDOG | NORMAL (0)
APPERROR | NORMAL (0)
8.2 (cont.) INTERNAL FAIL CONTACT CHECK
INTERNAL FAIL contact (PSM terminal) — measure across contact | Contact OPEN = IED healthy (de-energised in fault)
8.3 PLANT RESTORATION
Check | Expected / Action | Result | Notes
Remove test connections from CT / VT terminals | Field CTs and VTs reconnected
Restore control voltage wiring | All control circuits normal
Remove CT secondary shorting links — verify not open | CT circuits intact
Verify IED measuring load current — LHMI Measurements | Compare to substation metering
Differential balance check under load — IOP ≤ 0.05 pu | T2WPDIF / T3WPDIF IOP confirmed
SSIMG (SF6) gas pressure normal (if fitted) | No gas alarm
SSIML (oil level) normal (if fitted) | No oil level alarm
Buchholz / sudden pressure relay reconnected (if isolated) | Relays restored to service
Cancel all outstanding LOTO permits | All permits cleared
Notify operations — IED returned to service | Operations informed

## 9. Files & Sign-Off
FILES INDEX & SIGN-OFF
OVERALL TEST RESULT (from Cover sheet)
Signed Overall Result | PASS
TEST ARTEFACTS INDEX
Artefact | File Name / SharePoint Location | Date Saved | Notes
PCM600 project file (.pcm) — as-left backup
Pre-test disturbance records / internal event log
Post-test disturbance records
Completed results template (this file)
Oscillography / disturbance records
Photographs / site notes
DEFECTS / FINDINGS LOG
# | Defect Description | Action Taken / Work Order | Closed
1
2
3
4
5
6
SIGN-OFF
Role | Name (print) | Signature | Date
Test Engineer
Witness (Operations)
Approving Engineer
Documentation Yes/No
Omicron test file on SharePoint
As Left Settings on Sharepoint
Prot Database Updated
Job closed in SAP