## 1. Cover
SEL-700G GENERATOR PROTECTION RELAY — TEST RESULTS TEMPLATE
1. RELAY IDENTIFICATION
Relay Type / Model | SEL-700G
Relay ID (RID)
Terminal ID (TID)
Serial Number
Firmware ID (FID)
Checksum ID (CID)
Protected Equipment (generator tag)
Site / Substation
Test Date
Test Engineer
2. GENERATOR AND CT/VT PARAMETERS
Parameter | Setting Label | Value | Units
Generator MVA Rating | MVA / INOM |  | MVA / A nominal
Generator Terminal Voltage (L-L) | VNOM_X |  | kV (primary)
Phase Rotation | PHROT | ABC | ABC / ACB
X-Side (Stator) CT Connection | CTCONY / DELTA_X | WYE | WYE / DELTA
X-Side CT Ratio — Primary | CTRX (primary) |  | A primary
X-Side CT Ratio — Secondary | CTRX (secondary) | 5 | A secondary
Y-Side (87 Input) CT Ratio — Primary | CTRY (primary) |  | A primary
Y-Side (87 Input) CT Ratio — Secondary | CTRY (secondary) | 5 | A secondary
Neutral CT Ratio — Primary | CTRN (primary) |  | A primary
Neutral CT Ratio — Secondary | CTRN (secondary) | 5 | A secondary
Main VT Ratio — Primary | PTRX (primary) |  | V primary
Main VT Ratio — Secondary | PTRX (secondary) |  | V secondary
VT Connection Type (X-side) | DELTA_X | WYE | WYE / DELTA
Differential TAP (X-side) | TAPX |  | A secondary
Differential TAP (Y-side) | TAPY |  | A secondary
3. TEST TOLERANCES (yellow cells are editable)
Voltage Magnitude Tolerance | 1 | %
Current Magnitude Tolerance | 1 | %
Angle Tolerance | 2 | degrees
Pickup Tolerance | 5 | %
Timing Tolerance | 5 | %
4. OVERALL TEST RESULT
Auto-calculated cross-check | INCOMPLETE |  |  | (auto only — see signed result)
SIGNED OVERALL RESULT | PASS |  |  | PASS / PASS WITH NOTES / FAIL

## 2. Equip & Refs
EQUIPMENT & REFERENCES
TEST EQUIPMENT USED
Equipment | Manufacturer / Model | Asset / Serial No. | Cal. Due
DOCUMENTS & DRAWINGS
Document | Title / Description | Document No. | Rev
Relay Settings File (.sel / AcSELerator QuickSet)
AC Elementary / Schematic
DC Control Schematic
Generator Protection Single-Line Diagram
Protection Coordination Study
Maintenance Work Order

## 3. Pre-Test
PRE-TEST CHECKS
3.1 COMMUNICATIONS & IDENTIFICATION
Check | Expected / Action | Result | Notes
Connect serial cable or Ethernet to relay | Terminal prompt '=' or '-' appears
Issue QUIT <Enter> — verify response header | RID and TID match asset register
Issue ACC <Enter> + Level 1 password | Access Level 1 granted
ENABLED LED illuminated (green, front panel) | LED ON = relay healthy and in service
Firmware ID (FID) — record string | Matches approved firmware version
Checksum ID (CID) — record string | Matches as-left CID from last test
3.2 RELAY SELF-TEST STATUS (issue STATUS or STA <Enter> at serial port or front-panel STATUS)
All items should show OK. 'W' prefix = warning (issue STA C to clear). Latched FAIL = protection disabled — investigate immediately. HALARM = latched hardware alarm bit. SALARM = pulsed software alarm bit.
Self-Test Item (Table 11.9) | Normal Range / Description | Status / Measured Value | Action if WARN or FAIL
FPGA — Mainboard (power up) | FPGA accepts program + correct version
FPGA — Mainboard (run time) | No data acquisition interrupt loss; CRC OK
GPSB — Backplane communications | GPSB not busy on entry to processing interval
HMI — Front-panel (power up) | 2-line: ID registers match; Touchscreen: diagnostics pass
RAM — External (power up) | Read/write test on system RAM
RAM — External (run time) | Read/write test on system RAM
RAM — Internal (power up) | Read/write test on CPU RAM
RAM — Internal (run time) | Read/write test on CPU RAM
NON_VOL — Data Flash (power up) | Checksum on critical data
NON_VOL — Data Flash (run time) | Checksum on critical data
CR_RAM — Critical RAM / settings (power up) | Checksum on active settings copy
CR_RAM — Critical RAM (run time) | Instruction matches FLASH image
I/O Board — CARD_C / CARD_D / CARD_E | ID register matches part number
Slot Z Board (power up) | ID register matches part number
Slot Z A/D Offset WARN | Normal: −50 to +50 mV — issue STA C to clear warn
Slot E Board (power up) | ID register matches part number
Slot E A/D Offset WARN | Normal: −50 to +50 mV — issue STA C to clear warn
+0.9 V supply | Normal: 0.855 – 0.945 V
+1.2 V supply | Normal: 1.152 – 1.248 V
+1.5 V supply | Normal: 1.35 – 1.65 V
+1.8 V supply | Normal: 1.71 – 1.89 V
+2.5 V supply | Normal: 2.32 – 2.68 V
+3.3 V supply | Normal: 3.07 – 3.53 V
+3.75 V supply | Normal: 3.48 – 4.02 V
+5.0 V supply | Normal: 4.65 – 5.35 V
−1.25 V supply | Normal: −1.16 to −1.34 V
−5.0 V supply | Normal: −4.65 to −5.35 V
Clock Battery | Normal: 2.3 – 3.5 V — issue STA C to clear warn
Clock Chip | Clock chip comms + timekeeping — issue STA C to clear warn
Clock Chip RAM | Clock chip static RAM — issue STA C to clear warn
RTD module (External/Internal) | Comm OK; no open/shorted inputs (if fitted)
SEL-2664 Field Ground Module | OK/FAIL — fibre comms + module status (if fitted)
CID file (configured IED description) | CID file accessible
HALARM relay word bit | Should be 0 — not continuously asserted
SALARM relay word bit | Should be 0 — not pulsed
Relay Enabled | Output: 'Relay Enabled'
3.3 CLOCK / TIME SYNCHRONISATION
Check | Expected / Action | Result | Notes
Issue TIM <Enter> — relay time | Within 5 s of reference clock
Issue DAT <Enter> — relay date | Correct calendar date
Time source shown (Internal / IRIG-B) | IRIG-B if time-code input connected
Synchronise clock if out of tolerance | TIME hh:mm:ss DATE mm/dd/yy
3.4 EVENT RECORDS (pre-test baseline)
Check | Expected / Action | Result | Notes
Issue HIS <Enter> — review event history | No unexplained trips/alarms since last test
Issue SER <Enter> — review SER log | No unexpected HALARM / SALARM events
Issue SUM <Enter> — event summary | Review; record most recent event number
Issue EVE <Enter> — most recent event report | Review for unexpected generator trips
3.5 SETTINGS VERIFICATION
Check | Expected / Action | Result | Notes
Issue SHOW <Enter> (or SHO G/P/L/R) — download settings | Match approved settings file
CTRX (X-side CT ratio) matches Cover sheet | As per relay data
CTRY (Y-side/87 CT ratio) matches Cover sheet | As per relay data
CTRN (neutral CT ratio) matches Cover sheet | As per relay data
PTRX (main VT ratio) matches Cover sheet | As per relay data
TAPX / TAPY (differential TAP values) | As per protection study
VNOM_X, INOM, PHROT match generator nameplate | As per generator data
E87, E87N, EREF, E64G, E64F enabling settings | Elements enabled per scheme
Active setting group correct (Group 1 or as applicable) | As per operating procedure
Settings unchanged since last test | No unauthorised changes

## 4. Analogue Inputs
ANALOGUE INPUT VERIFICATION — PRIMARY VALUE CHECK
Verify the relay reports the correct PRIMARY value (Injected Secondary × CT or VT ratio). Use METER <Enter> or front-panel METER > Fundamental. All relay readings are in PRIMARY units (CTRX × secondary, etc.).
4.1 X-SIDE PHASE CURRENTS (IAX, IBX, ICX — stator CTs in Slot Z) [CTRX]
Ratio: Ratio_CTRX ¦ Tolerance: TolI_pct (defined names on Cover sheet)
Channel | Injected Sec. (A or V) | Inj. Angle (°) | Expected Primary (auto) | Relay Primary Reading | Relay Angle Reading | Mag Err % | Angle Err ° | Mag Tol % | Ang Tol ° | P/F
IAX — A-Phase X-side | [7 empty] | 1 | 2 | —
IBX — B-Phase X-side | [7 empty] | 1 | 2 | —
ICX — C-Phase X-side | [7 empty] | 1 | 2 | —
4.2 Y-SIDE PHASE CURRENTS (IAY, IBY, ICY — 87 input CTs in Slot E) [CTRY]
Ratio: Ratio_CTRY ¦ Tolerance: TolI_pct (defined names on Cover sheet)
Channel | Injected Sec. (A or V) | Inj. Angle (°) | Expected Primary (auto) | Relay Primary Reading | Relay Angle Reading | Mag Err % | Angle Err ° | Mag Tol % | Ang Tol ° | P/F
IAY — A-Phase Y-side (87 CT) | [7 empty] | 1 | 2 | —
IBY — B-Phase Y-side (87 CT) | [7 empty] | 1 | 2 | —
ICY — C-Phase Y-side (87 CT) | [7 empty] | 1 | 2 | —
4.3 NEUTRAL CURRENT (IN — neutral CT in Slot Z) [CTRN] (if neutral CT fitted)
Ratio: Ratio_CTRN ¦ Tolerance: TolI_pct (defined names on Cover sheet)
Channel | Injected Sec. (A or V) | Inj. Angle (°) | Expected Primary (auto) | Relay Primary Reading | Relay Angle Reading | Mag Err % | Angle Err ° | Mag Tol % | Ang Tol ° | P/F
IN — Generator neutral current | [7 empty] | 1 | 2 | —
4.4 VOLTAGE INPUTS (VAX, VBX, VCX — X-side VTs) [PTRX] (if VT card fitted)
Ratio: Ratio_PTRX ¦ Tolerance: TolV_pct (defined names on Cover sheet)
Channel | Injected Sec. (A or V) | Inj. Angle (°) | Expected Primary (auto) | Relay Primary Reading | Relay Angle Reading | Mag Err % | Angle Err ° | Mag Tol % | Ang Tol ° | P/F
VAX — Phase A voltage (X-side) | [7 empty] | 1 | 2 | —
VBX — Phase B voltage (X-side) | [7 empty] | 1 | 2 | —
VCX — Phase C voltage (X-side) | [7 empty] | 1 | 2 | —
4.5 DIFFERENTIAL METER CHECK (front-panel METER > Differential or EVE DIF <Enter>)
Under balanced load: IOP (operate) ≈ 0.00 TAP, IRT (restraint) ≈ load current in TAP units. If IOP/IRT > 0.10, investigate CT polarity, TAPX/TAPY balance, and CT connections. Check also 2nd-harmonic content (I1F2) — should be < 10% during normal load.
Diff Element | IOP (Operate, TAP) | IRT (Restraint, TAP) | MM = IOP/IRT | Accept if MM ≤ 0.10 | 2nd Harm I1F2 (TAP) | 5th Harm I1F5 (TAP) |  |  |  | Result
87-1 (DIFF1) |  |  |  | ≤ 0.10 | [5 empty] | —
87-2 (DIFF2) if used |  |  |  | ≤ 0.10 | [5 empty] | —
87-3 (DIFF3) if used |  |  |  | ≤ 0.10 | [5 empty] | —

## 5. Binary IO
BINARY I/O VERIFICATION
5.1 DIGITAL INPUTS — Pickup Verification
Apply rated control voltage to each input. Use front-panel MAIN > Targets > Row 49 or serial TARGET command. Verify IN101/IN102 state changes 0→1 when voltage applied.
Input No. | Function Label | Control Voltage Applied | Relay Word Bit | Result
IN101 | Digital Input 1 (Slot A) — edit to match schematics |  | IN101
IN102 | Digital Input 2 (Slot A) — edit to match schematics |  | IN102
IN301 | Optional DI — Slot C Input 1 (if card fitted) |  | IN301
IN302 | Optional DI — Slot C Input 2 (if card fitted) |  | IN302
IN303 | Optional DI — Slot C Input 3 (if card fitted) |  | IN303
IN304 | Optional DI — Slot C Input 4 (if card fitted) |  | IN304
5.2 DIGITAL OUTPUTS — Continuity Test
Force each output via serial (OUT101:=1 etc.) or front-panel CONTROL menu. Verify continuity through wiring to trip coil / alarm annunciator / close circuit. Restore all SELOGIC equations after test.
Output No. | Function Label | Force Command | Expected Result | P/F
OUT101 | TRIP / Main trip (edit label) | OUT101:=1 | Contact closes — continuity to trip coil
OUT102 | Alarm / Auxiliary (edit label) | OUT102:=1 | Contact closes — continuity verified
OUT103 | Close / Auxiliary (edit label) | OUT103:=1 | Contact closes — continuity verified
OUT301 | Optional DO — Slot C 1 (if fitted) | OUT301:=1 | Contact closes — continuity verified
OUT302 | Optional DO — Slot C 2 (if fitted) | OUT302:=1 | Contact closes — continuity verified

## 6. Element Tracker
PROTECTION ELEMENT TRACKER
Do not test all the elements, try and test a few them and alternate to do different elements each time.
Consider using the spare relay to Type Test a firmware version or protection setting scheme.
# | Element ID | Description | Enabled (Y / N / NA) | Tested | Result
1 | 87-1 | Phase Differential restrained — element 1 (87AP × TAPX)
2 | 87-1 U | Phase Differential unrestrained — element 1 (U87P × TAPX)
3 | 87-2 | Phase Differential — element 2 (if E87 enables 2nd element)
4 | 87-3 | Phase Differential — element 3 (if E87 enables 3rd element)
5 | 87N | Ground Differential (87NAP, 87NBP)
6 | REF | Restricted Earth Fault (50REF1P, REF1TC) — if EREF := Y
7 | 64G-1 | 100% Stator Ground — 27TH element 1 (64G1P, 64G1D) — if E64G := Y
8 | 64G-2 | 100% Stator Ground — 27TH element 2 (64G2P, 64G2D) — if E64G := Y
9 | 64F | Field Ground (via SEL-2664 module) — if E64F := Y
10 | 40Z1 | Loss of Field — zone 1 (40Z1P, 40Z1D)
11 | 40Z2 | Loss of Field — zone 2 (40Z2P, 40Z2D)
12 | 49T | Thermal Overload (49TP, 49TAP, 49TTC)
13 | 49RTD | RTD Thermal Protection (RTDT, RTDFLT) — if E49RTD fitted
14 | 46 | Current Unbalance / Negative-Sequence (46Q1P, 46Q2P, 46Q1D)
15 | 24D1 | Volts/Hz Definite Time 1 (24D1P, 24D1D)
16 | 24D2 | Volts/Hz Definite Time 2 (24D2P, 24D2D)
17 | 24C | Volts/Hz Inverse Time (24IP, 24IC)
18 | 78 | Out of Step (78P — loss-of-synchronism)
19 | 78VS | Vector Shift (78VSP — delta-angle loss-of-synchronism)
20 | INAD | Inadvertent Energisation (EINAD — 50/27 logic)
21 | 21C | Compensator Distance (backup) (21CX)
22 | 51C | Voltage-Controlled Time OC (51CP, 51CV)
23 | 51V | Voltage-Restrained Time OC (51VP, 51VTC)
24 | 50PX1 | X-side Phase Instantaneous OC — Stage 1 (50PX1P)
25 | 50PX2 | X-side Phase Instantaneous OC — Stage 2 (50PX2P)
26 | 51PX | X-side Phase Time OC (51PXP, 51PXTC)
27 | 50GX1 | X-side Ground Instantaneous OC — Stage 1 (50GX1P)
28 | 51GX | X-side Ground Time OC (51GXP, 51GXTC)
29 | 50QX1 | X-side Neg-Seq Instantaneous OC — Stage 1 (50QX1P)
30 | 51QX | X-side Neg-Seq Time OC (51QXP, 51QXTC)
31 | 50N | Neutral Instantaneous OC (50NP, uses 67NnP relay word bits)
32 | 51N | Neutral Time OC (51NP, 51NTC)
33 | 67N | Directional Neutral OC (67NnP, if EDIRX := Y)
34 | 27X1 | Undervoltage — element 1 (27X1P, 27X1T) — requires VT card
35 | 27X2 | Undervoltage — element 2 (27X2P, 27X2T) — requires VT card
36 | 27I | Inverse-Time Undervoltage (E27I, 27V1X) — requires VT card
37 | 59X1 | Overvoltage P — element 1 (59X1P, 59X1T) — requires VT card
38 | 59X2 | Overvoltage Q — element 2 (59X2P, 59X2T) — requires VT card
39 | 59X3 | Overvoltage G — element 3 (zero-seq) — requires VT card
40 | 59I | Inverse-Time Overvoltage (E59IX) — requires VT card
41 | 32X | Directional Power (reverse/low-forward) (32XP, 32XPWR)
42 | 81X1 | Over/Underfrequency — element 1 (81X1P, 81X1T) — requires VT card
43 | 81X2 | Over/Underfrequency — element 2 (81X2P, 81X2T) — requires VT card
44 | 81RX | Rate-of-Change of Frequency (81RX, E81RX) — requires VT card
45 | BFX | Breaker Failure — X-side (BFIX, BFTX, BFDX)
46 | 60LOPX | Loss of Potential (LOPBLKX, LOPPUX) — requires VT card
47 | 25X | Synchronism Check — X-side (25C, 25AX1, 25AX2) — if E25X := Y

## 7. Element Results
PROTECTION ELEMENT TEST RESULTS
Setting column = relay pickup setting (secondary A, V, TAP pu, or %). Measured Pickup = value at which relay output asserted. Pickup Err % = auto-calculated. Result = PASS if ¦Err¦ ≤ TolPickup_pct.
Just fill in the elements that you have tested, its not required to do all the elemts, try different elements each time make sure settings and firmware are the same.
Element | Description | Pickup Setting (sec A, V, or TAP pu) | Measured Pickup | Pickup Err % | Measured Time (s) | Result
87-1 R | Differential restrained pickup — 87AP × TAPX (TAP pu) |  |  |  |  | —
87-1 U | Differential unrestrained pickup — U87P × TAPX (TAP pu) |  |  |  |  | —
87N | Ground differential pickup — 87NAP (TAP pu) |  |  |  |  | —
REF | Restricted Earth Fault pickup — 50REF1P (A secondary, if enabled) |  |  |  |  | —
64G-1 | Stator ground 27TH — element 1 pickup (V secondary) |  |  |  |  | —
64G-2 | Stator ground 27TH — element 2 pickup (V secondary) |  |  |  |  | —
40Z1 | Loss of Field — zone 1 pickup (% Z secondary) |  |  |  |  | —
40Z2 | Loss of Field — zone 2 pickup (% Z secondary) |  |  |  |  | —
49T | Thermal Overload pickup — 49TP (A secondary) |  |  |  |  | —
46 | Current Unbalance — 46Q1P (A negative-sequence secondary) |  |  |  |  | —
24D1 | Volts/Hz — 24D1P (%, i.e. V/Hz relative to rated) |  |  |  |  | —
24C | Volts/Hz inverse — 24IP (%) |  |  |  |  | —
78 | Out of Step — 78P (% Z secondary) |  |  |  |  | —
78VS | Vector Shift — 78VSP (degrees) |  |  |  |  | —
INAD | Inadvertent Energisation — 50PXP (A secondary) |  |  |  |  | —
21C | Compensator Distance — 21CX (% Z secondary) |  |  |  |  | —
51C | Voltage-Controlled TOC pickup — 51CP (A secondary) |  |  |  |  | —
51V | Voltage-Restrained TOC pickup — 51VP (A secondary) |  |  |  |  | —
50PX1 | X-side Phase Inst OC — Stage 1 (A secondary) |  |  |  |  | —
50PX2 | X-side Phase Inst OC — Stage 2 (A secondary) |  |  |  |  | —
51PX | X-side Phase TOC pickup (A secondary) |  |  |  |  | —
50GX1 | X-side Ground Inst OC — Stage 1 (A secondary) |  |  |  |  | —
51GX | X-side Ground TOC pickup (A secondary) |  |  |  |  | —
50QX1 | X-side Neg-Seq Inst OC — Stage 1 (A secondary) |  |  |  |  | —
51QX | X-side Neg-Seq TOC pickup (A secondary) |  |  |  |  | —
50N | Neutral Instantaneous OC — 50NP (A secondary) |  |  |  |  | —
51N | Neutral TOC pickup — 51NP (A secondary) |  |  |  |  | —
27X1 | Undervoltage — element 1 (V secondary) |  |  |  |  | —
27X2 | Undervoltage — element 2 (V secondary) |  |  |  |  | —
59X1 | Overvoltage — element 1 (V secondary) |  |  |  |  | —
32X | Directional Power — 32XPWR (kVA secondary) |  |  |  |  | —
81X1 | Frequency — element 1 (Hz) |  |  |  |  | —
81X2 | Frequency — element 2 (Hz) |  |  |  |  | —
81RX | Rate-of-Change of Frequency (Hz/s) |  |  |  |  | —
BFX | Breaker Failure — BFDX timer (s) |  |  |  |  | —
25X | Synchronism Check — 25C closing window (degrees) |  |  |  |  | —

## 8. Post-Test
POST-TEST CHECKS
8.1 SETTINGS RESTORE & VERIFICATION
Check | Expected / Action | Result | Notes
Issue SHOW — verify settings unchanged | Match approved settings file
All test-forced SELOGIC equations restored | OUT101:=, SV variables correct
Active setting group restored to normal | Group 1 or as applicable
ENABLED LED illuminated (green) | Relay in service
8.2 FINAL SELF-TEST (STATUS / STA Command)
Check | Expected / Action | Result | Notes
Issue STA <Enter> — all items OK | No WARN or FAIL items
HALARM = 0 (no latched hardware alarm) | Relay word bit confirmed 0
SALARM = 0 (no software alarm pulsing) | Normal operating condition
Relay Enabled confirmed | 'Relay Enabled' in STA output
8.3 CLEAR TEST DATA BUFFERS
Issue the serial commands below to clear data generated during testing. This prevents test data from contaminating operational event records.
Serial Command | Action Performed | Completed | Notes
SUM R <Enter> | Reset event report and Summary Command buffers
SER R <Enter> | Reset Sequential Events Record buffer
LDP C <Enter> | Clear Load Profile Data
HIS C <Enter> | Clear event history (if required by procedure)
GSH R <Enter> | Reset Gene Autosynch Report (if synch check equipped)
8.4 PLANT RESTORATION
Check | Expected / Action | Result | Notes
Remove test connections from CT / VT terminals | Field CTs and VTs reconnected
Restore control voltage wiring | All control circuits normal
Remove CT secondary shorting links | CT circuits not open-circuited
Verify relay measuring load current — METER command | Compare to substation metering
METER DIF check — IOP/IRT ≤ 0.10 under load | Differential balance confirmed
SEL-2664 Field Ground Module Rf reading recorded | Normal: 20 000 kΩ (healthy field)
Cancel all outstanding LOTO permits | All permits cleared
Notify operations — relay returned to service | Operations informed

## 9. Files & Sign-Off
FILES INDEX & SIGN-OFF
OVERALL TEST RESULT (from Cover sheet)
Signed Overall Result | PASS
TEST ARTEFACTS INDEX
Artefact | File Name / SharePoint Location | Date Saved | Notes
Relay settings file (.sel / AcSELerator QuickSet project)
Pre-test event records (HIS, SER, EVE, SUM)
Post-test event records
Completed results template (this file)
Oscillography / disturbance records (EVE D)
Generator Autosynchronism Reports (CGSR / GSH)
Photographs / site notes
DEFECTS / FINDINGS LOG
# | Defect Description | Action Taken / Work Order | Closed
1
2
3
4
5
6
SIGN-OFF
Role | Name (print) | Signature | Date
Test Engineer
Witness (Operations)
Approving Engineer
Documentation yes/No Notes
Omicron test file on SharePoint
As Left Settings on Sharepoint
Prot Database Updated
Job closed in SAP