## 670 Check Sheet
ABB RELION 670 IED — BIENNIAL (2-YEARLY) VISUAL CHECK SHEET (REG670 / RET670)
1. IED AND SITE INFORMATION
IED Model | REG670 / RET670 (circle one)
Protected Equipment
Site / Substation
IED Name (Station / Bay)
Panel / Cubicle Tag
Work Order No.
Date of Check
Technician Name
Next Check Due | (2 years from date above)
2. CONNECTION METHOD
OPTION A — LHMI only (no laptop): The RET/REG670 has a full graphical touchscreen or keypad LHMI. Navigate with arrow keys / touchscreen. Main menu accessible from the LHMI home screen. OPTION B — Ethernet + PCM600 laptop: Connect laptop Ethernet to IED front port (RJ45). Open PCM600 → Online > Signal Monitor for live values. IP address from LHMI: Main menu → Settings → Communication → Ethernet. OPTION C — Ethernet + web browser: Navigate to IED IP address in browser (if web server enabled).
Connection method used today | LHMI only / Ethernet + PCM600 / Ethernet + browser (delete as applicable)
3. SELF-TEST AND IED STATUS (INTERRSIG self-supervision)
LHMI path: Main menu → Diagnostics → IED status → Signals → INTERRSIG. All signals should show NORMAL (0). A FAIL signal asserts the INTERNAL FAIL contact on the PSM. Hardware modules: Main menu → Diagnostics → Hardware → Module status.
Check Item | LHMI Path / How to Read | Expected | Result | Notes
Normal LED (green, fixed) | Visual — front panel upper-left LED | Green, solid
No alarm LEDs active | Visual — front panel LED indicators (15 programmable LEDs) | All off (or known/accepted)
INTERRSIG — FAIL signal | LHMI: Main menu → Diagnostics → IED status → Signals | NORMAL (0)
INTERRSIG — WARNING signal | Same path as above | NORMAL (0)
INTERRSIG — RTCERROR (clock error) | Same path as above | NORMAL (0)
INTERRSIG — TIMESYNCHERROR | Same path as above | NORMAL (0)
INTERRSIG — WATCHDOG | Same path as above | NORMAL (0)
INTERNAL FAIL contact (PSM terminal) | Measure across PSM INTERNAL FAIL output terminals | Contact OPEN (IED healthy)
PSM module status | LHMI: Main menu → Diagnostics → Hardware | OK
BIM / BOM / TRM module status | LHMI: Main menu → Diagnostics → Hardware | OK
Internal events — any recent FAILs? | LHMI: Main menu → Diagnostics → IED status → Internal events | No unexplained FAIL events
4. ANALOGUE MEASUREMENTS (Primary Values)
LHMI: Main menu → Measurements → [function block, e.g. T2WPDIF, GENPDIF, OC4PTOC] → monitored data. All values displayed in primary units. Record current load values below. PCM600: Signal Monitor shows live primary values.
Quantity | LHMI Path / Function Block | Measured Value | Unit | Notes
IA — Phase A Current (W1) | Measurements → [SMAI/CT function] → IA |  | A primary
IB — Phase B Current (W1) | Measurements → [SMAI/CT function] → IB |  | A primary
IC — Phase C Current (W1) | Measurements → [SMAI/CT function] → IC |  | A primary
IA — Phase A Current (W2 / Y-side) | Measurements → [SMAI W2] → IA (if 2nd CT set) |  | A primary
IB — Phase B Current (W2 / Y-side) |  |  | A primary
IC — Phase C Current (W2 / Y-side) |  |  | A primary
VA — Phase A Voltage | Measurements → [voltage function] → VA (if VT fitted) |  | kV primary
VB — Phase B Voltage | (if VT fitted) |  | kV primary
VC — Phase C Voltage | (if VT fitted) |  | kV primary
Frequency | Measurements → [voltage function] → frequency |  | Hz
5. CLOCK AND TIME SYNCHRONISATION
Check | LHMI Path | IED Value | Reference | Difference / OK?
IED Date and Time | Main menu → Diagnostics → IED status → Time (or Configuration → Time) |  | Today's date / current time
Time source (IRIG-B / IEEE 1588 / NTP) | Main menu → Diagnostics → IED status → Time source |  | IRIG-B or IEEE 1588 preferred
TIMESYNCHERROR = NORMAL | Main menu → Diagnostics → IED status → Signals |  | NORMAL
Time difference (accept ≤ 1 s with sync; ≤ 10 s internal) | Compare LHMI time to GPS/phone reference |  | ≤ 1 s
6. RECENT EVENTS (record most recent disturbance records / events)
LHMI: Main menu → Events → Disturbance records list (most recent first). PCM600: Event viewer shows all logged events with timestamps. Record the most recent events; flag any unexplained trips or alarms.
Event # (most recent = 1) | Date | Time | Event Description / Type
1
2
3
4
5
6
7
8
9
10
11
12
Total disturbance records stored (as displayed on LHMI)
7. DCS / ABB 800XA COMMUNICATION CHECK
Open the IED faceplate in the ABB 800XA control system. Verify live values (currents, IED status indicators) are updating. The 800XA communicates via IEC 61850 GOOSE / MMS. No yellow or red communication alarm objects should be present.
Check | Description | Result (Y / N) | Notes
800XA faceplate opened | Navigate to IED faceplate in 800XA Plant Explorer
IED Status = HEALTHY / OK | Green status indicator on faceplate — not alarm/fault colour
Live current values updating | Measured currents on faceplate match LHMI readings (not frozen)
No communication alarm | No yellow/red GOOSE or MMS communication alarm objects
800XA object path (record below) | e.g. 'Site / Substation / Relay Tag / Faceplate'
8. OPTIONAL — CLEAR EVENT BUFFERS (only if required by your procedure)
Only clear events if required by site procedure. Ensure all events have been downloaded/recorded BEFORE clearing. LHMI: Main menu → Events → [select event] → Clear (or Clear all). Internal events (INTERRSIG log) clear automatically after 40 events (FIFO).
Action | LHMI Path | Performed? (Y / N / N/A) | Notes
Download disturbance records | PCM600 → Disturbance handling → Save to file
Clear disturbance records | LHMI: Main menu → Events → Clear disturbance records
9. OBSERVATIONS AND CORRECTIVE ACTIONS
10. SIGN-OFF
Role | Name (print) | Signature | Date
Technician
Supervisor / Witness

## 615 Check Sheet
ABB RELION 615 IED — BIENNIAL (2-YEARLY) VISUAL CHECK SHEET (REF615 / RET615 / REM615 / REU615)
1. IED AND SITE INFORMATION
IED Model | REF615 / RET615 / REM615 / REU615 (circle one)
Protected Equipment
Site / Substation
IED Name
Panel / Cubicle Tag
Work Order No.
Date of Check
Technician Name
Next Check Due | (2 years from date above)
2. CONNECTION METHOD
OPTION A — LHMI only: The 615 series has a basic text-display LHMI (4 lines). Use the push-buttons (← → ↑ ↓ and Enter/C) to navigate menus. Main menu appears on pressing the MENU/HOME button. OPTION B — Ethernet + PCM600 laptop: Connect Ethernet to the front RJ45 port (if available on your model). Open PCM600 → Online monitoring for live values. Default IP is on the IED nameplate or in LHMI: Main menu → Configuration → Communication → Ethernet. OPTION C — Ethernet + web browser: Newer 615 C/D models support a built-in web server — navigate to IED IP address in a browser.
Connection method used today | LHMI only / Ethernet + PCM600 / Ethernet + browser (delete as applicable)
3. SELF-TEST AND IED STATUS
Key LED indicators on front panel: READY (green, solid) = IED healthy and in service. START (yellow) = protection element picked up (may be normal under load). TRIP (red) = protection has tripped. Self-supervision: LHMI: Main menu → Monitoring → Self-supervision → IED status.
Check Item | How to Read / Where to Look | Expected | Result | Notes
READY LED (green, solid) | Visual — front panel. Solid green = IED healthy | Solid green ON
No unexpected TRIP LED (red) | Visual — front panel red LED | Off (or explained by recent fault)
No alarm indication on LHMI display | Text display — check for error or alarm message on home screen | No error messages
IED self-supervision — IED status | LHMI: Main menu → Monitoring → Self-supervision → IED status | HEALTHY / OK
Internal fault indicator | LHMI: Main menu → Monitoring → Self-supervision → Internal fault | No internal faults
Power supply OK | LHMI: Main menu → Monitoring → Self-supervision | PSU OK
Communication module (if IEC 61850 fitted) | LHMI: Main menu → Monitoring → Self-supervision → IEC 61850 | OK / No error
4. ANALOGUE MEASUREMENTS (Primary Values)
LHMI: Main menu → Monitoring → Measurements → Current (or Voltage). All values shown in primary units. PCM600 Signal Monitor also displays live primary values. Record current values. Flag anything obviously abnormal (e.g. one phase zero while others are loaded).
Quantity | LHMI Path | Measured Value | Unit | Notes
IL1 — Phase L1 Current (primary) | Monitoring → Measurements → Current → IL1 |  | A primary
IL2 — Phase L2 Current (primary) | Monitoring → Measurements → Current → IL2 |  | A primary
IL3 — Phase L3 Current (primary) | Monitoring → Measurements → Current → IL3 |  | A primary
I0 / IN — Residual Current | Monitoring → Measurements → Current → I0 |  | A primary
UL1 — Phase Voltage (primary) | Monitoring → Measurements → Voltage → UL1 (if VT fitted) |  | kV primary
UL2 — Phase Voltage (primary) | (if VT fitted) |  | kV primary
UL3 — Phase Voltage (primary) | (if VT fitted) |  | kV primary
Frequency | Monitoring → Measurements → Frequency (if VT fitted) |  | Hz
5. CLOCK AND TIME SYNCHRONISATION
Check | LHMI Path | IED Value | Reference | Difference / OK?
IED Date and Time | LHMI: Main menu → General settings → Date and time (or shown on LHMI home screen) |  | Today's date / current time
Time source (IRIG-B / SNTP / Internal) | LHMI: Main menu → Configuration → Time synchronisation |  | IRIG-B or SNTP preferred
Time difference (accept ≤ 10 s) | Compare LHMI time to GPS / phone reference |  | ≤ 10 s
6. RECENT EVENTS (record most recent events from the event list)
LHMI: Main menu → Events → Event list (most recent first). PCM600: Event viewer. Record the most recent events. Flag any unexplained TRIP or FAULT events.
Event # (most recent = 1) | Date | Time | Event Description / Type
1
2
3
4
5
6
7
8
9
10
11
12
Total events in event list (as shown on LHMI)
7. DCS / ABB 800XA COMMUNICATION CHECK
Open the IED faceplate in the ABB 800XA control system. Verify live values and IED status are updating. The 615 series typically communicates via IEC 61850, DNP3.0, or Modbus. No yellow or red communication alarm objects should be present on the 800XA faceplate.
Check | Description | Result (Y / N) | Notes
800XA faceplate opened | Navigate to IED faceplate in 800XA Plant Explorer
IED Status = HEALTHY / OK on faceplate | Green status indicator — not alarm/fault colour
Live current values updating | Measured currents on faceplate match LHMI readings (not frozen or zero under load)
No communication alarm | No yellow/red comms alarm objects on faceplate
800XA object path (record below) | e.g. 'Site / Substation / Relay Tag / Faceplate'
8. OPTIONAL — CLEAR EVENTS (only if required by your procedure)
Only clear events if required by site procedure. Download/record all events BEFORE clearing. LHMI: Main menu → Events → Event list → Clear all (or select individual events).
Action | LHMI Path | Performed? (Y / N / N/A) | Notes
Download event list | PCM600 → Event viewer → Export / Save
Clear event list | LHMI: Main menu → Events → Event list → Clear all
9. OBSERVATIONS AND CORRECTIVE ACTIONS
10. SIGN-OFF
Role | Name (print) | Signature | Date
Technician
Supervisor / Witness